## Cost Abstract
COST ABSTRACT OF WORKS FOR THE CONSTRUCTION OF POLICE HEAD QUARTER BUILDING AT NAYA RAIPUR
Sr. No. | Description of Items | Amount in INR
|  | In Figures | In Words
A | Civil Works | 0
B | Public Health engineering and Fire fighting Works | 0
C | Electrical Works | 0
D | HVAC Works | 0
Total Amount |  | 0

## P - A (Civil)
BILL OF QUANTITY
PART A : CIVIL WORKS
Sr. No. | Description of Items | Unit | Quantity | Rate In INR | Rate In Words | Amount In INR
EARTH WORK:
1 | Excavation for all types and sizes of foundations, trenches and drains or for any other purpose including disposal of excavated stuff upto 1.5 m lift and lead upto 50m (at least 5m away from the excavated area), including dressing and leveling of pits, including execution of work in or under water and/or liquid mud and pumping out of water.
a | In all types of soil | Cum | 49045 |  |  | 0
b | In ordinary rock | Cum | 5450 |  |  | 0
2 | Extra for every additional lift of 1.5m or part of there of
a | In all types of soil | Cum | 2488 |  |  | 0
b | In ordinary rock or hard rock | Cum | 276 |  |  | 0
3 | Surface dressing of the ground including removing vegetation and making up undulation and in-equalities not exceeding 15 cm depth/height including disposal of rubbish up to 1.5 m lift & lead up to 50 m.(All kinds of soil). | SQM | 51370 |  |  | 0
4 | Clearing jungle including uprooting of rank vegetation, grass brush wood, trees and saplings of girth up to 30 cm measured at a height of 1 m above ground level and removal of rubbish up to a distance of 50m outside the periphery of the area cleared. | SQM | 35959 |  |  | 0
5 | Clearing grass and removal of the rubbish up to a distance of 50 m outside the periphery of the area cleared. | SQM | 15411 |  |  | 0
6 | Filling from available excavated earth (Excluding rock) in trenches, plinth, sides of foundation etc. in layers not exceeding 20cm in depth consolidating each deposited layer by ramming and watering with a lead up to 50 M. and lift up to 1.5 M. | Cum | 51631 |  |  | 0
7 | Providing and filling in plinth with sand/ Crusher dust under floor in layers not exceeding 20cm in depth consolidating each deposited layer by ramming and watering, including dressing etc. complete | Cum | 4025 |  |  | 0
8 | Supplying chlorpyriphos/ Lindane emulsifiable concentrate of 20% in sealed containers including delivery as specified.
a | Supplying of clorphyriphos | litre | 6150 |  |  | 0
9 | Diluting chemical emulsion (Chlorpyriphos/ lindane) in water as per manufacturers recommendation and injecting for pre-constructional curative cum preventive anti-termite treatment: (Five year service guarantee bond to be signed by contractor)
a | Surface treatment by spreading emulsion under floor, over the plinth area before laying base concrete @ 5 litres / sqm. | sqm | 15650 |  |  | 0
b | Treatment of inside of plinth masonry wall on using diluted chemical emulsion @ 1.5 litre per hole, including drilling 12 mm diameter holes in plinth wall below plinth protection at the intervals of 300 mm and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand). | RM | 7350 |  |  | 0
c | Treatment of outer side of plinth masonry wall using diluted chemical emulsion @ 1.5 litre per hole, including drilling 12 mm diameter holes in plinth wall at the junction of floor at the intervals of 300 mm and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand). | RM | 1590 |  |  | 0
10 | Carriage by mechanical transport for 5 km lead including loading and unloading all complete as per direction of Engineer incharge
a | Earth | Cum | 1700 |  |  | 0
11 | Extra for mechanical transport for every one km or part thereof beyond first 5 km lead over and above item no. 10 a. all complete as per direction of Engineer incharge . | cum | 285 |  |  | 0
12 | Carriage by mechanical transport for 1 km lead: for Miscellanious work including loading and unloading all complete as per direction of Engineer incharge | Cum | 1700 |  |  | 0
CENTERING & SHUTTERING WORK:
13 | Providing and fixing formwork including centering, shuttering, strutting, staging, propping bracing etc. complete and including its removal at all levels, for:
a | Foundations, footings, base of columns and plinth beam in any shape and size. | sqm | 7800 |  |  | 0
b | Wall of any thickness including attached pilasters, buttresses etc. | sqm | 4850 |  |  | 0
c | Columns, Pillars, Piers and likes- rectangular or square in shape | sqm | 6737 |  |  | 0
d | Beams, lintels, cantilevers & walls | Sqm | 21380 |  |  | 0
e | Suspended floors, roofs, access platform, balconies (plain surfaces),slab etc. | Sqm | 32010 |  |  | 0
CEMENT CONCRETE (Plain & reinforced conc.)
14 | Providing and laying nominal mix cement concrete with crushed stone aggregate using concrete mixer in foundation, plinth and at ground level excluding cost of form work
a | 1:4:8 (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size). | cum | 1410 |  |  | 0
15 | Providing and laying nominal mix cement concrete with crushed stone aggregate using concrete mixer in all works upto floor five level excluding cost of form work.
a. | PCC for floors(Mix 1:3:6) | cum | 1162 |  |  | 0
b | 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size). | cum | 1510 |  |  | 0
16 | Providing and laying design mix reinforcement cement concrete with crushed graded stone aggregate 20mm nominal size using batching plant, transit mixer and concrete pump, in all works upto floor five level excluding cost of reinforcement and form work.
a. | M-20 (using minimum cement 390 kg/cum concrete) | Cum | 176 |  |  | 0
b | M-25 (using minimum cement 410 kg/cum concrete) | Cum | 8845 |  |  | 0
c | M-30 (using minimum cement 410 kg/cum concrete) | Cum | 806 |  |  | 0
17 | Providing and Placing in position reinforcement for R.C.C. work including straightening, cutting, bending, binding etc. complete as per drawings including cost of binding wire all complete:
| Thermo-Mechanically treated bars | MT | 1050 |  |  | 0
18 | Providing and laying damp proof course (upto 50mm thick) with plain cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded crushed stone aggregate 20mm nominal size) including formwork. | cum | 51 |  |  | 0
19 | Providing and mixing water proofing material in cement concrete work @ 1 kg per 50kg of cement. | kg | 24800 |  |  | 0
20 | Applying a coat of hot bitumen 30/40 using @ 1.7kg/ sqm on damp proof course after cleaning the surface with brushes and finally with a piece of cloth lightly soaked in kerosene oil. | sqm | 850 |  |  | 0
21 | Making 50mm thick plinth protection of plain cement concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded crushed stone aggregate 20mm nominal size) over 75mm bed of dry brick ballast 40mm nominal size well rammed and consolidated and grouted with sand including finishing the top smooth. | sqm | 932 |  |  | 0
22 | Providing and fixing aluminium strip 1.60 mm thick on expansion joints with iron screws as per design to match the colour, shade of wall treatment . | sqm | 110 |  |  | 0
23 | Providing and fixing in position 25mm thick impregnated fibre board confirming to IS: 1838 in expansion joints, including cost of primer, sealing compound all complete. | sqm | 360 |  |  | 0
WATER PROOFING WORK:
24 | Providing and laying integral cement based water proofing treatment on roofs, balconies, terraces etc with average thickness of 120mm and minimum thickness at khurra as 65 mm, consisting of following operations including surface preparation: | sqm | 12756 |  |  | 0
i) Applying a slurry coat of neat cement using 2.75 kg/sqm. of cement mixed with water proofing compound conforming to IS. 2645 over the RCC slab including adjoining walls upto 300mm height.
ii) Laying brick bats with mortar using broken bricks/brick bats 25 mm to 115mm size with 50% of cement mortar 1:5 (1 cement : 5 coarse sand) mixed with water proofing compound conforming to IS : 2645 over 20 mm thick layer of cement mortar of mix 1:5 (1 cement :5 coarse sand ) mixed with water proofing compound conforming to IS : 2645 to required slope and treating similarly the adjoining walls upto 300 mm height including rounding of junctions of walls and slabs.
iii) After two days of proper curing applying a second coat of cement slurry using 2.75kg/ sqm of cement admixed with water proofing compound conforming to IS : 2645.
iv) Finishing the surface with 20 mm thick joint less cement mortar of mix 1:4 (1 cement :4 coarse sand) mixed with water proofing compound conforming to IS : 2645 including laying glass fibre cloth of approved quality in top layer of plaster and finally finishing the surface with trowel with neat cement slurry and making pattern of 300x300 mm square 3mm deep.
v) The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test. All above operations to be done in order:
25 | Providing and laying water proofing treatment to vertical and horizontal surfaces of depressed portions of WC, kitchen and the like consisting of: | sqm | 700 |  |  | 0
i) 1st course of applying cement slurry @ 4.4 Kg/sqm mixed with water proofing compound conforming to IS 2645 including rounding off junction of vertical and horizontal surface.
ii) 2nd course of 20mm cement plaster 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound including rounding off junction of vertical and horizontal surface.
iii) 3rd course of applying blown or residual bitumen applied hot @ 1.7 Kg. per sqm of area.
iv) 4th course of 400 micron thick PVC sheet. (Overlaps at joints of PVC sheet should be 100 mm wide and pasted to each other with bitumen @ 1.7 Kg. per sqm of area.
26 | Filling in shunken floors of toilets etc with cinder including necessary compaction as directed by EIC with all leads & lifts for all floors. | Cum | 129 |  |  | 0
27 | Providing & placing in position suitable PVC water stops conforming to IS:12200 for construction/ expansion joints between two RCC members and fixed to the reinforcement with binding wire before pouring concrete etc. complete:
| Dumb bell with central bulb (180mm wide, 8mm thick). | RM | 200 |  |  | 0
BRICK WORK
28 | Brick Work with modular fly-ash lime bricks (FALG Bricks) conforming to IS:12894-2002 of class designation 40 in foundations and plinth in:
a | Cement mortar 1:6 (1 cement: 6 Sand) | cum | 600 |  |  | 0
29 | Brick Work with modular fly-ash lime bricks (FALG Bricks) conforming to IS:12894 -2002 of class designation 40 in superstructure above plinth and upto floor five level in:
a | Cement mortar 1:6 (1 cement: 6 Sand) | cum | 3880 |  |  | 0
30 | Half Brick thick masonary with modular fly-ash lime bricks (FALG Bricks) conforming to IS:12894 of class designation 40 in 100mm thick partiton wall above plinth upto floor level five:
a | Cement mortar 1:4 (1 cement: 4Sand) | Sqm | 4865 |  |  | 0
b | Extra forproviding and placing in position hopping 25x1.60mm or 2 nos 6mm dia bars reinforcement at every third course of half brick masonary. | Sqm | 5350 |  |  | 0
31 | Moulding and cornices with brick masonry using bricks of crushing strength not less than 35 kg/sqcm and water absorption not more than 20% in cement Mortar 1:4 (1 cement 4 coarse sand) including cement plaster 15 mm thick, 10 cm projected, 20 cm deep (40 cm Girth) in cement mortar 1:4 (1 cement : 4 fine sand) at any floor. | RM | 1536 |  |  | 0
WOOD WORK:
32 | Providing and fixing flush door shutters decorative type, core of block board construction with frame of first class hard wood and well matched commercial ply veneering with vertical grains or cross bands and face veneers on both faces of shutters excluding hinges.
(a) | 40mm thick single leaf door ( Phenol formaldehyde binding) | sqm | 134 |  |  | 0
(b) | 35mm thick single leaf door ( Phenol formaldehyde binding) | sqm | 513 |  |  | 0
33 | Extra over 32(a) for double leaf instead of single leaf | sqm | 30 |  |  | 0
34 | Providing and fixing lipping with second class teak wood lipping (40 x 12 mm size) on all edges of shutters. | RM | 170 |  |  | 0
35 | Providing and fixing lipping with second class teak wood lipping (35 x 12 mm size) on all edges of shutters. | RM | 1538 |  |  | 0
36 | Extra for providing vision panel not exceeding 0.10 Sqm in all type of flush shutters (excluding cost of glass) | No | 112 |  |  | 0
37 | Extra for providing louvers in flush doors upto 0.20 sqm | No | 48 |  |  | 0
38 | Providing and fixing stainless steel sliding door bolts with 16mm rod, 2.5mm thick flap, necessary stainless steel nuts bolts and screws etc complete.(Size-300mm) | No | 48 |  |  | 0
39 | Providing and fixing stainless steel tower bolts (Barrel type) with necessary stainless steel screws etc complete (Size 250X10mm) | No | 434 |  |  | 0
40 | Providing and fixing stainless steel door handles having flap thickness 2.5mm, necessary stainless steel screws etc complete | No | 552 |  |  | 0
41 | Providing and fixing stainless steel hanging door stopper with necessary stainless steel screws complete.(double) | No | 217 |  |  | 0
42 | Providing and fixing stainless steel fixed stopper with necessary stainless steel screws complete.(50mm long) | No | 217 |  |  | 0
43 | Providing and fixing stainless steel door latch with 12mm rod, 2.5mm thick flap, necessary stainless steel screws etc complete | No | 107 |  |  | 0
44 | Providing and fixing IS: 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc complete | No | 38 |  |  | 0
STEEL & ALUMINIUM WORK:
45 | Steel work welded in built up sections/ framed work including cutting, hoisting, fixing in position and applying a priming coat of red oxide zinc chromate primer:
(a) | In gratings, frames, guard bar, ladder, railings, brackets, gates and similar works. | kg | 54500 |  |  | 0
46 | Providing and fixing in position doors, windows and ventilators frames made of cold rolled pressed steel sheet framed profiles made from commercial M.S. Sheets conforming to I.S. 513 of 1973 and as per general specifications of I.S 4351 including hinges jamb, lock jamb, steel butt hinges, base tie, joints mitred and welded with 10cm long legs of size 15x3mm M.S. flat, embedded in cement concrete blocks 15x10x10cm size of grade M-10 or rawl plugs and screws or with fixing clips or with bolts and nuts including neatly compacted filling M-10 cement concrete in profile section applying a priming coat of red oxide zinc chromate primer.
(a) | Single rebate 100mmx50mm size, 1.25mm thick sheet. | metre | 1572 |  |  | 0
47 | Supplying and fixing rolling shutter of approved makes made of M.S. laths interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and out side locking with push and pull arrangement complete but excluding the cost of top cover and spring.
(a) | 80x1.25mm M.S. Laths | sqm | 27 |  |  | 0
48 | Providing and fixing 27.5cm long wire spring for rolling shutters. | No | 6 |  |  | 0
49 | Providing and fixing M.S. sheet top cover for rolling shutter:
a | 1.25mm thick | sqm | 18 |  |  | 0
50 | Providing and fixing ball bearing for rolling shutters. | No | 6 |  |  | 0
51 | Providing and fixing mechanical device chain and crank operation for operating rolling shutters | set | 3 |  |  | 0
52 | Extra for providing grilled rolling shutter manufactured out of 8 mm dia. M.S. bar instead of laths as per approved design (area of grill provided, only to be measured) | sqm | 4.5 |  |  | 0
53 | Providing stainless steel railing/ grill made of S.S. flats, hollow S.S. pipe or square/ rectangular sections of approved design fixing in stair case, balcony or other places with metal fasteners and stainless steel bolts etc complete. | kg | 5652 |  |  | 0
54 | Providing and fixing aluminium work for doors, windows, ventilators and partitions made out of extruded aluminium standard sections (main section with minimum 1.5mm thickness) conforming to IS: 733, IS: 1285 mitred and jointed mechanically including aluminium cleats, neoprene weather stripping gasket beveled edge beading, screws duly fixed in wall/ floor with fixing clips or hold fasteners or bolts and nuts as required aluminium sections shall be anodized transparent or dyed to approved shade according to IS: 1868, minimum anodic coating shall be of grade AC-15. (Glazing and panelling to be paid for separatel
(a) | For fixed portion (qty as given below) | Kg | 6140 |  |  | 0
55 | For shutter of doors, windows & ventilators including providing and making provision for fixing of fitting wherever required including the cost of PVC/ neoprene gasket required (Fittings shall be paid for separately).(qty as given below) | kg | 6140 |  |  | 0
56 | Providing & fixing float glass panes of 6 mm thickness | Sqm | 1400 |  |  | 0
57 | Extra for providing and fixing Solar control glass panes in aluminium door, window, ventilator shutters and partitions instead of float glass.
| 6 mm thickness | Sqm | 1300 |  |  | 0
58 | Providing & fixing Toughened Solar Control Glass 12 mm (including Glass) with all accessories.
| 12mm thick toughened Glass D/W | Sqm | 670 |  |  | 0
59 | Providing and fixing of six/seven levers branded and approved mortise lock for D/W | No | 169 |  |  | 0
60 | Providing and fixing of floor spring IS: marked (Everite, Door link or any equivalent make) with stainless steel cover plate including cutting and making good the floor etc. complete. | No | 40 |  |  | 0
ROOFING & CEILING:
61 | Providing gola 75x75 mm in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 stone aggregate 10mm and down grade) including finishing with cement mortar 1:3 (1 cement : 3 fine sand) as per standard design. | RM | 1860 |  |  | 0
62 | Making khurras 45x45 cm with average minimum thickness of 5 cm cement concrete 1:2:4 (1 cement : 2 sand : 4 graded stone aggregate of 20 mm nominal size) over P.V.C. Sheet 1mx1mx400micron, finished with 12mm cement plaster 1:3 (1 cement: 3 sand) and a coat of neat cement rounding the edge sand: making and finishing the outlet complete. | each | 54 |  |  | 0
63 | Providing and fixing at all height false ceiling consisting of frame work "W" / "U" / "L" sections made of G.I. sheet with zinc coating of grade 120 consisting of angle cleats of size 25mm wide x 1.6mm thick with flanges of 22mm and 37mm at 1200mm centre to centre one flange fixed to the ceiling with dash fastener 12.5mm diax40mm long with 6mm dia bolts to the angle hangers of 25x25x0.55mm of required length, and other end of angle hanger being fixed with nut and bolts to G.I. channels 45x15x0.9mm running at the rate of 1200mm centre to centre to which the ceiling section 0.5mm thick button wedge of 80mm with tapered flanges of 26mm each having clips of 10.5mm at 450mm centre to centre shall be fixed in a direction perpendicular to G.I. channel with connecting clips made out of 2.64mm diax230mm long G.I. wire at every junction including - | sqm | 6430 |  |  | 0
Fixing the gypsum board with ceiling section and perimeter channels 0.55mm thick 27mm high having flanges of 20mm and 30mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450mm centre to centre with 25mm long drive-all screws @ 230mm interval including jointing and fixing to a flush finish of tapered and square edges of the board with recommended filler, jointing tapes, finisher and two coats of primer suitable for board as per manufactures specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed all complete as per drawing and specification and direction of the Engineer in Charge but excluding the cost of painting with 12.5 mm thick tapered edge gypsum board conforming to IS: 2095- Part I.
PLASTERING & POINTING:
64 | Providing & applying 6mm thick cement plaster 1:3 (1 cement : 3 fine sand) on ceilings of RCC slab & beam as approved Engineer incharge. | Sqm | 9800 |  |  | 0
65 | Providing and applying 12mm thick plaster with cement mortar of mix ratio 1:4 (1 cement : 4 sand) , to internal surfaces of concrete, masonry work including jambs, sills, grooves, pattas, rounding of corners, etc. all complete as per architectural drawings, specifications and finished smooth with wooden rundha at all height, leads and lifts, providing, erecting and dismantling independent double-legged scaffolding, raking out joints, hacking concrete surfaces, providing and and cleaning of surfaces, curing, etc. complete to the satisfaction of the EIC. | Sqm | 29050 |  |  | 0
66 | Extra for20mm thick raised or sunk cement mortar band/drip course in cement mortar 1:4 as per drawing | RM | 2304 |  |  | 0
67 | 18mm thick cement plaster in two coats with under layer of 12mm thick plaster 1:5 (1 cement : 5 fine sand) and top layer of 6mm thick with cement plaster 1:3 (1 cement : 3 fine sand) finished rough with sponge complete as per architectural drawing & design. | Sqm | 17800 |  |  | 0
68 | Providing and fixing chicken mesh weighting not less than 250 gms/ sqm as per IS : specification in the required width with 10mm long steel nails on vertical and horizontal surface near R.C.C. and brick walls junctions including scaffolding and all lead and lifts etc. complete before plastering upto 10mts in height. | Sqm | 14055 |  |  | 0
69 | Providing and applying plaster of paris putty(punning) over plastered wall surface including scaffolding complete up to 2 mm thickness to make surface even and smooth in line and level. | Sqm | 7575 |  |  | 0
FLOORING:
70 | Providing and laying vitrified floor tiles with double charge/ multi charge printing with water absorption less than 0.5% and conforming to IS : 15622 of approved make in all colours and shades and size mentioned below (+/- 10mm), laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with white cement and matching pigments etc. complete:Size 600x600mm.
| Size 600x600mm | Sqm | 7610 |  |  | 0
71 | P&F Chequerred terrazzo tiles 25 mm thick with graded marble chips of size up to 6mm in floors on 25mm thick bed of cement mortar 1:6 (1 cement : 6 coarse sand) jointed with neat cement slurry mixed with pigment to match the shade of tiles including grinding rubbing and polishing complete
(a) | Light shade using white cement- | Sqm | 120 |  |  | 0
72 | Providing & Fixing Granite stone 15mm thick (sample of granite stone for flooring shall be approved by engineer-in-charge) over 20mm (average) thick base of cement mortar 1:4 (1 cement :4 sand) laid and jointed with white cement slurry mixed with pigment of required shade to match the shade of stone complete. (area of slab over 0.50 sqm) (Item to be executed only as per drawings & specifications) | Sqm | 1765 |  |  | 0
73 | P/F 15 mm thick Table rubbed polished Black Granite stone slab in risers and treads of steps skirting dado and pillars laid on 12mm (average) thick base of cement mortar 1:3 (1 cement : 3 coarse sand) and jointed with grey cement slurry including rubbing and polishing etc. complete (single stone is to be used for risers and treads of steps and width of stone for skirting and dado shall be equal to the height of skirting & dado and length of 1.0 m | Sqm | 1865 |  |  | 0
74 | Extra for nosing in granite stone for treads | RM | 990 |  |  | 0
75 | P/F 25 mm thick KOTA stone slab flooring over 20mm (average) thick base of cement mortar 1:4 laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab including grinding rubbing and polishing etc. complete (Area of slab to be over 0.20 sq.m and up to 0.50 sq.m) | sqm | 13500 |  |  | 0
76 | P/F KOTA stone slab 25mm thick in risers and treads of steps, skirting dado and pillar laid in 12mm (average) thick cement mortar 1:3 (1 cement : 3 coarse sand) and jointed with grey cement slurry mixed with pigment to match the shade of the slab including rubbing and polishing complete. (Single stone is to be used for riser and treads of steps and the width of stone for skirting and dado shall be equal to the height of skirting/ dado with a minimum length of 1.0 M.) | Sqm | 590 |  |  | 0
77 | Extra for nosing in steps and treads of kota stone slab. | RM | 1531 |  |  | 0
78 | 25mm thick Local RAJIM/ Red Flag stone slab flooring laid over 20mm (average) thick base of cement mortar 1:6 (1 cement : 6 coarse sand) laid over & jointed with grey cement slurry mixed with pigments to match the shade of the stone i/c grinding, rubbing and polishing. | Sqm | 310 |  |  | 0
79 | Extra for laying of any type of stone in flooring strips up to 100mm width.
| Upto 100 mm width | sqm | 300 |  |  | 0
80 | Providing and laying in required position 40mm thick IPS flooring of cement concrete 1:2:4 (1cement: 2course sand: 4graded stone aggrigate) finished with a floating coat of neat cement including cement slurry, as per drawings & specifications and as approved by EIC. | sqm | 1310 |  |  | 0
81 | Providing and fixing Ist quality ceramic glazed wall tiles conforming to IS : 15622 (thickness to be specified by the manufacturer ) of approved make in all colours, shades except burgundy, bottle green, black of any size as approved by Engineer-in-Charge in skirting, risers of steps and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with pigment of matching shade complete as approved by EIC and as per drawings & specifications. ( | sqm | 4355 |  |  | 0
82 | Providing and laying rectified ceramic glazed floor tiles 300x300mm conforming to IS : 15622 of approved make, colour, shade laid on 20 mm thick Cement Mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement mixed with matching pigment etc., complete (In colours such as White, Ivory, Grey, Fume Red Brown,) | Sqm | 2300 |  |  | 0
84 | Providing and laying Antiskid ceramic glazed floor tiles of size 300x300mm with water absorption's less than 0.5% and conforming to IS : 15622 of approved make , laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with white cement and matching pigments etc. complete: | sqm | 555 |  |  | 0
85 | Providing & laying 60mm thick precast interlocking grass paver concrete blocks of approved size (approx 305 sqcm) and shape/ pattern, over 40 mm thick average complete coarse sand bed with joints of 3mm thick filled by fine sand including leveling with surface vibrator, temping and sweeping etc. complete of minimum compressive strength of 250 kg/sq.cm. Make : Ultra /Unistone | Sqm | 970 |  |  | 0
MARBLE WORK /WALL LINING.
86 | 15mm thick black Granite work (machine cut, table rubbed & mirror polished) for wall lining (veneer work) in cement mortar 1:3 (1 cement : 3 coarse sand) including pointing with cement mortar 1:2 (1 white cement: 2 marble dust) mixed with matching pigment. (Area of slab should be over 0.5 sqm). | sqm | 1218 |  |  | 0
87 | 15mm thick black Granite work (machine cut, table rubbed & mirror polished) for kitchen platform, vanity counters, window sills and similar locations of required size laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) including joints treated with white cement mixed with matching pigment including rubbing and polishing to edge moulding to give high gloss finish. | sqm | 70 |  |  | 0
88 | Extra for fixing marble /granite stone in facia and drops of width upto 150 mm with epoxy resin based adhesive instead of cement mortar including cleaning etc. complete | RM | 75 |  |  | 0
89 | Extra for making opening of required size & shape for wash basins/ kitchen sink in kitchen platform, vanity counters and similar location in marble/Granite/stone work including making necessary holes for pillar taps etc. including rubbing and polishing of cut edges etc. complete. | No | 32 |  |  | 0
DISTEMPERING PAINTING & FINISHING
90 | Wall painting with acrylic luxury emulsion (plastic) paint (top most approved brand quality) to give an even shade.
(a) | On new work (Two or more coats) | Sqm | 50530 |  |  | 0
91 | Preparation of wall surface by applying a coat of Cement Based Wall Care Putty of Birla / JK sand papering and making the surface smooth to proper shape and presentable conditions. | Sqm | 68330 |  |  | 0
92 | Applying one coat of cement primer on wall surface. | Sqm | 68330 |  |  | 0
93 | Painting old exterior surface (one or more coats) with PREMIUM SMOOTH EMULSION paint as per manufacturer's specifications to give protective and decorative finish including cleaning washing of surface etc. complete with
(a) | On new work (Two or more coats) | sqm | 17800 |  |  | 0
94 | Painting on new work (two or more coats) to give an even shade with:
(a) | Satin synthetic enamel paint (top most approved brand quality) | sqm | 13220 |  |  | 0
SPECIAL & MISCELLANEOUS ITEMS OF WORK:
95 | Supplying and fixing hollow metal steel fire doors flush type of 2 hours fire rating and approved colour approved by EIC as per specification outlined below, all material and labour complete in all respects conforming to IS: 3614 ( PART 2) Door frames shall be of double rebate profile of size 143 mm x 57mm with a bending radius of 1.4 mm made out of 1.6 mm thick galvanized steel sheet (16 gauge) and the steel door hutter shall be double skin door made out of 1.25mm thick galvanized steel sheet (18 gauge) conforming to IS: 277- 1981.The infill material shall be resin bonded oneycomb paper with thermal insulation. The rate shall include applying 2 coats of fire resistant synthetic enamel paint over a coat of primer including all materials and labour complete as approved by EIC.(
| Two hr fire rated door at GF FD(2.1X1.5) | No | 12 |  |  | 0
96 | Providing & Fixing 10mm thick Bison board (water proof fibre reinforced cement board) on the duct work, shafts etc. as per design & drawing and directions engineer in charge complete with fixing devices and finishing. | sqm | 845 |  |  | 0
EXTERNAL DEVELOPMENT WORK:
97 | Precast interlocking concrete paver blocks: Providing & laying factory made confirm technical specification of Bureau of Indian Standards 15658 of 2006 of heavy duty pavers resulting in consistent and uniform quality, rubber moulded, white cement based , pigmented block lacquer coating and cured through drying process mechanically vibrated and compacted precast interlocking premium concrete paver blocks in M40 grade , 60mm thickness of approved size, design and colour with providing and laying in position over 40 mm thick average complete coarse sand bed with joints of 3mm thick filled by fine sand including leveling with surface vibrator, temping and sweeping etc. complete Make : Ultra / Eurocon / Duracrete;
| Coloured precast interlock concrete block | sqm | 15550 |  |  | 0
Compacting Original Ground
98 | Compacting Original Ground supporting embankment Loosening, leveling and compacting original ground to facilitate placement of first layer of embankment , scarified to a depth of 150 mm , mixed with water at O.M.C.and then compacted by rolling so as to achieve minimum dry density as given in table 300-2 for embankment construction. | cum | 1070 |  |  | 0
99 | Construction of embankment / sub grade with Material Obtained from Borrow Pits (Construction of embankment with approved material/selected soil having C.B.R. > 5 (unless specified otherwise in the contract) obtained from borrow pits with all lifts and leads, transporting to site, spreading, grading to required slope and compacting to meet requirement of table 300-2) | cum | 1070 |  |  | 0
100 | Footpaths and Separators (Construction of footpath/ separator by providing a 150 mm compacted granular sub base as per clause 401 and 25 mm thick cement concrete grade M15, over laid with pre-polished cement concrete floor tiles confirm to IS 1237:1980 (Reaffirmed in 1996) for heavy duty tiles (Exterior Grade) of 22-25mm thick in cement mortar 1:4 including provision of all drainage arrangements but excluding kerb channel..) as per pattern, size and colour as approved by engineer Make of concrete tiles : Ultra / Eurocon / Duracrete; | sqm | 1900 |  |  | 0
101 | Granular Sub-base as per Table:- 400-1
Construction of granular sub-base by providing close graded Material, , carriage of mixed Material to work site, spreading in uniform layers with motor grader on prepared surface watering, rolling and compacting with vibratory power roller at OMC to achieve the desired density, complete as per clause 401
Plant mix method
| For grading- III Material | cum | 1070 |  |  | 0
102 | Dry Lean Cement Concrete Sub- base (Construction of dry lean cement concrete Sub- base over a prepared sub-grade with coarse and fine aggregate conforming to IS: 383, the size of coarse aggregate not exceeding 25 mm, aggregate cement ratio not to exceed 15:1, aggregate gradation after blending to be as per table 600-1, cement content not to be less than 150 kg/ cum, optimum moisture content to be determined during trial length construction, concrete strength not to be less than 10 Mpa at 7 days, mixed in a batching plant, transported to site, laid with a paver with electronic sensor, compacting with 8-10 tonnes vibratory roller, finishing and curing.)
a | With vibratory roller | cum | 475 |  |  | 0
103 | Cement Concrete Pavement (Construction of un-reinforced, dowel jointed, plain cement concrete pavement over a prepared sub base with 43 grade cement @ 400 kg per cum, coarse and fine aggregate conforming to IS 383, maximum size of coarse aggregate not exceeding 25 mm, mixed in a batching and mixing plant as per approved mix design, transported to site, laid with a fixed form or slip form paver, spread, compacted and finished in a continuous operation including provision of contraction, expansion, construction and longitudinal joints, joint filler, separation membrane, sealant primer, joint sealant, debonding strip, dowel bar, tie rod, admixtures as approved, curing compound, finishing to lines and grades as per drawing) | cum | 950 |  |  | 0
104 | Cast in Situ Cement Concrete M 20 Kerb with Channel (Construction of cement concrete kerb with channel with top and bottom width 115 and 165 mm respectively, 250 mm high in M 20 grade PCC on M10 grade foundation 150 mm thick, kerb channel 300 mm wide, 50 mm thick in PCC M20 grade, sloped towards the kerb, kerb stone with channel laid with kerb laying machine, foundation concrete laid manually, all complete . | meter | 1600 |  |  | 0
105 | Retro- reflectrorized Traffic signs (Providing and fixing of retro- reflectrorized cautionary, mandatory and informatory sign as per IRC :67 made of encapsulated lens type reflective sheeting vide clause 801.3, fixed over aluminum sheeting, 1.5 mm thick supported on a mild steel frame of size 40 x 40 x 5 mm and mild steel angle iron post 75 mm x 75 mm x 6 mm firmly fixed to the ground by means of properly designed foundation with M15 grade cement concrete 45 cm x 45 cm x 60 cm, 60 cm below ground level as per approved drawing)
a | 60 cm circular | each | 10 |  |  | 0
106 | Painting on Concrete Surfaces
| Two coats on new surfaces (Painting two coats after filling the surface with synthetic enamel paint in all shades on new plastered concrete surfaces) | sqm | 1108 |  |  | 0
107 | Painting Lines, Dashes, Arrows etc on Roads in Two Coats on New Work (Painting lines, dashes, arrows etc on roads in two coats on new work with ready mixed road marking paint conforming to IS:164 on bituminous surface, including cleaning the surface of all dirt, dust and other foreign matter, demarcation at site and traffic control )
a | Over 10 cm in width | sqm | 11 |  |  | 0
b | Up to 10 cm in width | sqm | 160 |  |  | 0
108 | G.I Barbed wire Fencing 1.2 meter high (Providing and fixing 1.2 meters high GI barbed wire fencing with 1.8 m angle iron posts 40 mm x 40 mm x 6 mm placed every 3 meters center to center founded in M15 grade cement concrete, 0.6 meter below ground level, every 15th post, last but one end post and corner post shall be strutted on both sides and end post on one side only and provided with 9 horizontal lines and 2 diagonals interwoven with horizontal wires, fixed with GI staples, turn buckles etc complete as per clause 807 ) | RM | 160 |  |  | 0
109 | PCC 1:3:6 in Foundation (Plain cement concrete 1:3:6 mix with crushed stone aggregate 40 mm nominal size mechanically mixed, placed in foundation and compacted by vibration including curing for 14 days.) | cum | 4 |  |  | 0
110 | Providing and laying Reinforced Cement Concrete pipe NP 4 / prestrssed concrete pipe on first class bedding (Laying Reinforced cement concrete pipe NP4 /prestressed concrete pipe for culverts on first class bedding of granular material including fixing collar with cement mortar 1:2 but excluding excavation, protection works, backfilling, concrete and masonry works in head walls and parapets . )
| 600 mm dia | meter | 42 |  |  | 0
Horticulture & Land scaping work
111 | Trenching in ordinary soil upto a depth of 60cm including removal and stacking of serviceable materials and then disposing of by spreading and neatly levelling with in a lead of 50m and making up the trenched area to proper levels by filling with earth or earth mixed with sludge or/and manure before and after flooding trench with water (excluding cost of imported earth, sludge or manure) | cum | 500 |  |  | 0
112 | Supplying and stacking of good earth at site including royalty, loading, unloading and carriage upto 10 km (earth measured in stacks will be reduced by 20% for payment). | cum | 6500 |  |  | 0
113 | Supplying and stacking sludge at site including royalty, loading, unloading and carriage upto 10 km (sludge measured in stacks will be reduced by 8% for payment). | cum | 1624 |  |  | 0
114 | Supplying and stacking at site well decayed cow dung manure from approved source, including loading, unloading and carriage upto 10 km (manure measured in stacks will be reduced by 8% for payment) : | cum | 1624 |  |  | 0
115 | Rough dressing the trenched ground including breaking clods | sqm | 750 |  |  | 0
116 | Spreading of sludge, dump manure or/and good earth in required thickness (Cost of sludge, dump manure or/ and good earth to be paid separately | cum | 6000 |  |  | 0
117 | Mixing earth and sludge or manure in proportion specified or directed. | cum | 6496 |  |  | 0
118 | Grassing with ‘Doob’ grass including watering and maintenance of the lawn for 30 days or more till the grass forms a thick lawn free from weeds and fit for mowing including supplying good earth if needed (the good earth shall be paid for separately
(a) | In rows 15 cm apart in either direction | sqm | 19975 |  |  | 0
119 | Preparation of beds for hedging and shrubbery by excavating 60cm deep and trenching the excavated base to a further depth of 30cm, refilling the excavated earth after breaking clods and mixing with sludge or manure in the ratio of 8:1 (8 parts of stacked volume of earth after reduction by 20% : one part of stacked volume of sludge or manure after reduction by 8%), flooding with water, filling with earth if necessary, watering and finally fine dressing, levelling etc. including stacking and disposal of materials declared unserviceable and surplus earth by spreading and levelling as directed, within a lead of 50m lift upto 1.5 m complete (cost of sludge, manure or extra earth to be paid for separately). | cum | 450 |  |  | 0
120 | Digging holes in ordinary soil and refilling the same with the excavated earth mixed with manure or sludge in the ratio of 2:1 by volume (2 parts of stacked volume of earth after reduction by 20% : 1 part of stacked volume of manure after reduction by 8%) flooding with water, dressing including removal of rubbish and surplus earth, if any with all leads and lifts (cost of manure, sludge or extra good earth if needed to be paid for separately) : | No | 833 |  |  | 0
121 | Filling mixture of earth and sludge or manure in the desired proportion in trenches, flooding with water and levelling (cost of supplying earth and sludge or manure and mixing excluded). | cum | 300 |  |  | 0
122 | Providing and planting following herbs in garden including preparation of soil, base plantation, providing and spreading different fertilizers, soil and sand: a) Hedges like Alife, Dorenta, Tikoma etc. | No | 833 |  |  | 0
Other Miscelenaous Works
123 | Providing and fixing in true horizontal level 600mm x 600mm and 15mm thick modular acoustic false ceiling system equivalent to make and manufacturer "Armstrong World Industries or Equivalent" using hot dipped Galvanised Steel Section exposed surface with pre-coating capping, main Tee of size 24 x 32 mm at every 1200mm c/c maximum and rotary stitched cross tee of size 24 x 27 mm at every 600mm c/c and sub-cross tee of size 24 x 25mm at 1200mm c/c and wall angle of size 19 x 19mm fixed to periphery of the wall and the above grid is suspended at every 1200mm c/c in both directions using 2.0mm thick pre-straightened GI wire laying fine fissured butt edge ceiling tiles of 15mm thick mineral fibre board having RH 99% and for finished of size 600 x 600mm including cost & conveyance of all materials and labour charges such as cutting, fixing of standing of frame work exposing roof making complete for finished item of work. | Sqm | 6000 |  |  | 0
124 | Providing and fixing mirror for toilet of size as per drawings using 6mm thick mirror of Modifloat make SS studs, 25mm dia, of approved make stuck to wall/partitions. All edges of the mirror to be machine polished. The rate to be inclusive of necessary housings for lights in Aluminium extruded section at back side and the mirror and cutting mirror coating at locations as shown by the Architect, etc. complete. | sqm | 20 |  |  | 0
125 | Providing and fixing Acoustical Panelling which includes 12mm thick Celotax Glass Wool / Rock Wool boards stuck to 12mm thick commercial ply backing. The panelling to be finished with approved fire rated fabric with 4mm thick foam underlay. Rate for fabric Rs. 450/- per RMT. The rate to be inclusive of making grooves in 75 mm x 35 mm MDF and finished in approved Duco paint as per detailed drawings. All exposed edges to be in TW beading 8mm thick and finished in approved melamine. | sqm | 1800 |  |  | 0
126 | Providing and cladding in proper line and level Vitrified Tiles 600mm x 300mm x 8mm of approved make and sample in pattern as per detailed drawings in cement paste on a backing coat of cement mortar 1:3, not exceeding 12mm. The rate should be inclusive of granite round coping on top edge, corners etc. 15mm wide, polishing of exposed edges, cleaning joints and grouting them with neat white cement paste with pigmented additives to match shade of the tile etc. complete. | Sqm | 500 |  |  | 0
127 | Steel work in tubular structure in built-up sections, trusses and frame work including cutting, hoisting, fixing in position upto a height of 5m above plinth level, consisting of columns trusses, roof and bottom purlins, base plate, holding down bolts, wind ties bracing (if required), bolts, nuts and washers for fastening etc. complete with applying a priming coat of red oxide zinc chromate primer.
a | Electric resistance or induction butt welded tubes | Kg | 240000 |  |  | 0
128 | Providing and fixing clamps of required size and shape for anchoring stone wall lining to the baking or securing adjacent stone in stone wall lining in cement mortar 1:2 (1 cement : 2 coarse sand) including making the necessary chases and/or holes in stone/wall.
a | Stainless steel cramps with stainless steel nuts and bolts and washer (total weight not less than 260 gms). | Kg | 1267 |  |  | 0
129 | Providing and fixing commercial grade water proof ply for wall paneling on wooden frame with necessary nails complete as required.
a | 19mm | sqm | 465 |  |  | 0
130 | Providing and fixing approved shade veneering on wood wall paneling complete as required. | sqm | 465 |  |  | 0
131 | Providing & fixing double leaf sliding door with glass partion of size 7.2m (W)X 2.25m height made from 10mm frame less toughened glass consisting of 2 fixed leaves of size 2.1m(W)X2.25m(H) and 2 sliding leaves of size 1.5m(W)X2.25m(H) each specified by you with fitting accessories. | No | 4 |  |  | 0
132 | Providing and fixing in position homogeneous P.V.C. quartz reinforced floor covering tiles conforming to IS: 3462/1986 of size 300x300 mm over existing smooth and finished surface including removal of dust etc. from existing floor and laying approved adhesive (Dunlop S- 758, Fevicol SR 998 or equivalent) at the rate of 0.25 kg/ sqm including rolling with light wooden roller weighing about 5 kg. etc. complete.
a | 3 mm thick tiles (Weight 6 kg per sqm) | Sqm | 822 |  |  | 0
133 | CAR PARKING SHADE:
a | Providing and fixing in required profile twin wall 6mm thick Lexan thermo clean of approved make one side UV protected polycarbonate sheet in required colour & shade over existing M.S. tubular frame work and weather resistant Neoprin EPDM rubber gasket on both side of Alcox section 80 as to make the fabricated structure water proof. The Alcox section shall be rigidly to supporting frame work alongwith the sheet with self taping self drilling steel screws fixed approx 150mm centre to centre. The open end edges of Polycarbonate sheet shall be provided with aluminium channel of size 10x10x1.5mm and weight not less than 0.20Kg/m with necessary self taping screws. The joints of the structure shall be properly sealed with silicon sealants wherever required so as to make the fabricated structure totally water proof. The rate shall include the cost of all materials, such as aluminium Alcox section set and charnel, EPDM gasket, self taping screws, nuts bolts and silicon sealant and all the labour and material required to cut, fabricate and fix the structure complete as per direction of Engineer Incharge (Cost of supporting steel tubular structural frame work provided shall be paid for separately). Finished sheet area shall be measured for the purpose of payment. | sqm | 1820 |  |  | 0
SUB TOTAL OF PART A : CIVIL WORKS | [5 empty] | 0

## P - B (PHE & FF)
BILL OF QUANTITY
PART B : PUBLIC HEALTH ENGINEERING AND FIRE FIGHTING WORKS
Sr. No. | Description of Items | Unit | Quantity | Rate In INR | Rate In Words | Amount In INR
BUILDINGS : INTERNAL PLUMBING WORK
Section-1: Water Supply
1 | Providing and fixing 15 mm nominal bore uplasticised PVC connection pipe with C.P brass nuts collar and PVC bush of approved quality and colour:
(a) | 30 CM length | Nos | 554 |  |  | 0
2 | Providing and fixing C.I. dirt box strainer for bulk type water meter with nuts, bolts, rubber insertions etc. complete conforming to IS : 2373 :100 mm dia | Nos | 1 |  |  | 0
3 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes in concealed in wall, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints including cutting chases and making good the walls etc complete as per direction of Engineer in Charge.
(a) | 15mm dia nominal bore | Rm | 873 |  |  | 0
(b) | 20mm dia nominal bore | Rm | 279 |  |  | 0
(c ) | 25mm dia nominal bore | Rm | 119 |  |  | 0
(d) | 32mm dia nominal bore | Rm | 102 |  |  | 0
4 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes in trenches, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings. This included jointing of pipes & fittings with one step CPVC solvent:
(a) | 40mm dia nominal bore | Rm | 90 |  |  | 0
5 | Providing and laying in trenches G.I. pipes medium class complete with G.I. fittings including excavation of trenches, refilling the same and testing of joints complete:
(a) | 15mm dia nominal bore | Rm | 532 |  |  | 0
(b) | 20mm dia nominal bore | Rm | 570 |  |  | 0
(c ) | 25mm dia nominal bore | Rm | 2260 |  |  | 0
(d) | 32mm dia nominal bore | Rm | 711 |  |  | 0
(e) | 40mm dia nominal bore | Rm | 1089 |  |  | 0
(f) | 65mm dia nominal bore | Rm | 192 |  |  | 0
(g) | 80mm dia nominal bore | Rm | 165 |  |  | 0
6 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end):
(a) | 32 mm nominal bore | Nos | 11 |  |  | 0
(b) | 40 mm nominal bore | Nos | 19 |  |  | 0
(c ) | 50 mm nominal bore | Nos | 19 |  |  | 0
(d) | 65 mm nominal bore | Nos | 8 |  |  | 0
(e) | 80 mm nominal bore | Nos | 2 |  |  | 0
7 | Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete
(a) | 15 mm nominal bore | Nos | 57 |  |  | 0
(b) | 20 mm nominal bore | Nos | 50 |  |  | 0
(c ) | 25 mm nominal bore | Nos | 5 |  |  | 0
8 | Providing and fixing gun metal non- return valve (vertical type) of approved quality (screwed end) :
(a) | 40 mm nominal bore | Nos | 4 |  |  | 0
(b) | 65 mm nominal bore | Nos | 6 |  |  | 0
(c ) | 80 mm nominal bore | Nos | 2 |  |  | 0
9 | Providing and fixing enclosed type water meter (bulk type) conforming to IS : 2373 and tested by Municipal Board complete with bolts, nuts, rubber insertions etc. (The tail pieces if required will be paid separately) :
(a) | 100 mm nominal bore | Nos | 2 |  |  | 0
10 | Providing and Fixing 500LPD Evacuated Tube Collector Based Solar Water Heating System including electrical back up of 2kw, 3 nos, internal piping, pumps, control valves,MS angle frame of 40 X 5mm for foundation as specified and directed by engineer in charge. | Nos | 2 |  |  | 0
Section - II: Sanitary Fixtures
11 | Providing and fixing water closet squatting pan (Indian type W.C. pan), 100mm sand cast Iron P or S trap, 10 litre low level P.V.C. flushing cistern (same colour) conforming to IS : 7231, with flush bend and other fittings and fixtures complete including cutting and making good the walls and floors wherever required :
(a) | White Orissa pattern W.C. pan of size 580x440 mm | Nos | 20 |  |  | 0
12 | Providing and fixing vitreous china water closet (European type W.C. pan) with white ISI marked plastic seat and lid, 10 litre low level white P.V.C. flushing cistern (same colour), conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :
(a) | White pedestal type | Nos | 5 |  |  | 0
13 | Providing and fixing vitreous china water closet (European type W.C. pan) with white ISI marked plastic seat and lid, 10 litre low level white P.V.C. flushing cistern (same colour), conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :
(a) | White wall hung type | Nos | 109 |  |  | 0
14 | Providing and fixing one piece construction white vitreous china squatting plate urinal with an integral rim longitudinal flushing pipe, standard size G.I. flush pipe for back and front flush, C.P. brass coupling complete including cutting and making good the walls and floors etc. wherever required : | Nos | 54 |  |  | 0
15 | Providing and fixing one urinal flusher with battery operated | Nos | 54 |  |  | 0
16 | Providing and fixing Stainless Steel A ISI 304 (18/8) kitchen sink without drain board as per IS 13983 with C.I. brackets and stainless steel plug 40 mm including painting of fittings and brackets, cutting and making good the walls wherever required :
(a) | 610x510 mm bowl depth 200 mm. | Nos | 14 |  |  | 0
17 | Providing and fixing 600x450 mm beveled edge 4mm mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | Nos | 141 |  |  | 0
18 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 including C.P. brass extension if required:
(a) | Angle valve for (450gms) | Nos | 555 |  |  | 0
19 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 pillar cock with auto closing system.
(a) | Pillar cock with auto closing system | Nos | 129 |  |  | 0
20 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 including C.P. brass extension if required:
(a) | Long body bib cock (500gms) | Nos | 14 |  |  | 0
21 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 including C.P. brass extension if required:
(a) | Hand shower set with flexible extension pipe | Nos | 21 |  |  | 0
22 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 including C.P. brass extension if required:
(a) | Bottle trap set with extension pipes | Nos | 147 |  |  | 0
23 | Supply & fixing Soap dish plate ( SS type) | Nos | 27 |  |  | 0
24 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 including C.P. brass extension if required:
(a) | Towel rail (600mm long x 20mm dia) | Nos | 141 |  |  | 0
25 | Providing and fixing stone slab table rubbed, edges rounded and polished of size 75x50 cm deep and 1.8 cm thick fixed in urinal partitions by cutting a chase of appropriate width with chase cutter and embedding the stone in the chase with epoxy grout or with cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 6 mm nominal size) as per direction of Engineer-in-charge and finished smooth.
(a) | White Agaria Marble Stone. | Each | 35 |  |  | 0
26 | Providing and fixing PTMT liquid soap container 109mm wide, 125mm high and 112mm distance from wall of standard shape with bracket of the same materials with snap fittings of approved quality and colour. weighing not less than 105 gms. | Nos | 91 |  |  | 0
27 | Providing and fixing vitreous china pedestal for wash basin completely recessed at the back for the reception of pipes and fittings.
| White | Nos | 116 |  |  | 0
28 | Providing and fixing C.P. brass robe hooks (JAGUAR-CAT.NO-779) or equivalent including cutting and making good the walls wherever required complete to the satisfaction of Engineer in charge. | Nos | 129 |  |  | 0
29 | Providing and fixing CP brass hand shower (health faucets) with 8mm dia 1meter long flexible tube and wall hook/Jaquar or equivalent make CP or equivalent)with all fittings and fixtures complete inlcuding cutting and making good the walls and floors wherever required: | Nos | 56 |  |  | 0
Section-III: Soil Waste and Vent Pipes
30 | Providing fixing cast iron S&S pipe as per IS: 3989 for soil, waste and vent pipes including jointing, sealing, EPDM rubber gasket asper manufacturer's specifications complete:
(a) | 75 mm dia | Rm | 106 |  |  | 0
31 | Providing fixing and push on jointing sand cast iron S&S pipe as per IS: 3989 for soil, waste and vent pipes including EPDM rubber gasket complete:
(a) | 100 mm dia pipe. | Rm | 1675 |  |  | 0
32 | Providing fixing and push on jointing sand cast iron S&S single equal junction with access door of required degree as per IS: 3989, insertion rubber washer 3 mm thick, bolts and nuts including EPDM rubber gasket complete::
(a) | Single tee with door(110x110x110 mm) | Nos | 122 |  |  | 0
33 | Providing fixing and push on jointing sand cast iron S&S single unequal junction with access door of required degree as per IS: 3989, insertion rubber washer 3 mm thick, bolts and nuts including EPDM rubber gasket complete:
(a) | Bend 45° | Nos | 50 |  |  | 0
34 | Providing fixing and push on jointing sand cast iron S&S plain bend of required degree as per IS: 3989 including EPDM rubber gasket complete::
(a) | Plain bend | Nos | 159 |  |  | 0
35 | Providing and fixing on wall Vent cowl conforming to IS : 3989 (heavy) jointing with seal ring conforming to IS : 3989 leaving 10 mm gap for thermal expansion.
(a) | Vent cowl (100 mm) | Nos | 124 |  |  | 0
36 | Providing and fixing sand cast iron S&S trap of self cleansing design with screwed down or hinged grating with or without vent arm as per IS: 1729 complete, including cost of cutting and making good the walls and floors :
(a) | Multi floor trap 100 | Nos | 129 |  |  | 0
37 | Providing and fixing on wall surface G.I. pipes medium class complete with G.I. fittings and clamps, including cutting, making good the walls etc. and testing of joints complete:
(a) | 32mm dia nominal bore | Rm | 333 |  |  | 0
(b) | 40mm dia nominal bore | Rm | 60 |  |  | 0
38 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 including C.P. brass extension if required:
(a) | Shower rose (revolving type) (150mm) | Nos | 8 |  |  | 0
Section-IV: Sewerage and Drainage Systems
39 | Providing and laying non-pressure NP3 class (light duty) RCC pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 find sand) including testing of joints etc. complete.
(a) | 150mm dia RCC Pipe | Rm | 97 |  |  | 0
40 | Providing and laying cement concrete 1:5:10 (1 cement : 5 coarse sand : 10 graded stone aggregate 40 mm nominal size) all-round S.W. pipes including bed concrete 150mm thick as per standard design:
(a) | 150mm dia SW pipe | Rm | 97 |  |  | 0
41 | Constructing brick masonry chamber for underground C.I. inspection chamber and bends with 75 class designation bricks in cement mortar 1:4 (1 cement : 4 coarse sand) M.S lockable cover of 6mm thk M>S plate with angle frame of 35x35x4 R.C.C. top slab with 1:2:4 mix (1 cement :2 coarse sand : 4 graded stone aggregate 20 mm nominal size) foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished smooth with a floating coat of neat cement on walls and bed concrete etc. complete as per standard design :Inside dimensions 455x610 mm and 45 cm deep for single pipe line :
| With F.P.S. bricks | Nos | 64 |  |  | 0
42 | Providing and fixing square-mouth S.W. gully trap grade 'A'’ complete with C.I. grating brick masonry chamber with well burnt modular clay bricks crushing strength not less than 35kg/ cm², water tight C.I. cover with frame of 300 x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design :
(a) | 150 x 100 mm size P type. | Nos | 54 |  |  | 0
Section - V: Rain Water Pipes and Fittings
43 | Providing and fixing uPVC pipes as per IS:4985 class-4 including all fittings e.g. bends junctions, cowls, offsets, clean out plugs etc. jointing with solvent cement including cutting holes in walls, floors excavation, refilling and disposal of surplus earth wherever required and making good .
(a) | 160 mm dia | Rm | 594 |  |  | 0
EXTERNAL WORKS
Section - I: Sewer Works
44 | Excavation for all types and sizes of foundations, trenches and drains or for any other purpose including disposal of excavated stuff upto 1.5 m lift and lead upto 50m (at least 5m away from the excavated area), including dressing and leveling of pits.
(a) | In all types of soil | Cum | 1848.75 |  |  | 0
45 | Filling from available excavated stuff (Excluding rock) in trenches, plinth, sides of foundation etc. in layers not exceeding 20cm in depth consolidating each deposited layer by ramming and watering with a lead upto 50 M. and lift upto 1.5 M. | Cum | 380.8 |  |  | 0
46 | Removing excavated material (soils) to a distance exceeding 50m but not excceding 250m and depositing where directed at a level not exceeding 1.5 m above the starting point complete all as specified and directed.
(a) | soft/ distintegrared rock | Cum | 1467.95 |  |  | 0
47 | Providing and laying non-pressure NP3 class RCC pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 find sand) including testing of joints etc. complete.
(a) | 150mm dia RCC Pipe | Rm | 1700 |  |  | 0
(b) | 250mm dia RCC Pipe | Rm | 850 |  |  | 0
48 | Providing and laying cement concrete 1:5:10 (1 cement : 5 fine sand: 10 graded stone aggregate 40 mm nominal size) upto haunches of RCC pipes including bed concrete as per specifications.
(a) | 150mm dia RCC Pipe | Rm | 1080 |  |  | 0
(b) | 250mm dia RCC Pipe | Rm | 1470 |  |  | 0
49 | Constructing brick masonry manhole in cement mortar 1:4 ( 1 cement :4 coarse sand ) with R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size), inside plastering 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominalsize) finished with a floating coat of neat cement complete as per standard design : Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg), With Sewer bricks conforming to IS : 4885. | Nos | 82 |  |  | 0
50(a) | Extra for depth for manholes, size 90 x 80 cm with sewer bricks conforming to IS: 4885 | m | 25 |  |  | 0
50 | Constructing brick masonry circular type manhole 0.91m internal dia atbottom and 0.56m dia at top in cement mortar 1:4 (1 cement :4 coarse sand), in side cement plaster 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement,foundation concrete 1:3:6 mix (1 cement : 3 coarse sand : 6 graded stone aggregate 40mm nominal size), and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement, all complete as per standard design,0.91 m deep with S.F.R.C. cover and frame (heavy duty, HD-20 grade designation) 560mm internal diameter conforming to I.S. 12592, total weight of cover and frame to be not less than 182kg., fixed in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) including centering, shuttering all complete. (Excavation, foot rests and 12mm thick cement plaster at the external surface shall be paid for separately) : With Sewer bricks conforming to IS : 4885 | each | 32 |  |  | 0
51(a) | Extra depth for circular type manhole 0.91m internal dia (at bottom) beyond 0.91m to 1.67m, With Sewer bricks conforming IS : 4885 | m | 20 |  |  | 0
51 | Constructing brick masonry circular manhole 1.22m internal dia at bottom and 0.56m dia at top in cement mortar 1:4 (1 cement :4 coarse sand) inside cement plaster 12mm thick with cement mortar 1:3 (1 cement :3 coarse sand) finished with a floating coat of neat cement foundation concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40mm nominal size) and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement, all complete as per standard design : 1.68 m deep with SFRC Cover and frame (heavy duty HD- 20 grade designation) 560mm internal diameter conforming to I.S. 12592, total weight of cover and frame to be not less than 182kg. fixed in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including centering, shuttering all complete. (Excavation, foot rests and 12 mm thick cement plaster at the external surface shall be paid for separately) : With Sewer bricks conforming IS : 4885 | each | 19 |  |  | 0
52(a) | Extra depth for circular type manhole 1.22m internal dia (at bottom) beyond 1.68 m to 2.29 m : With Sewer bricks conforming IS : 4885 | m | 8 |  |  | 0
52 | Constructing brick masonry circular manhole 1.52 m internal dia at bottom and 0.56 m dia at top in cement mortar 1:4 (1 cement : 4 coarse sand) inside cement plaster 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement, foundation concrete 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 40mm nominal size) and making necessary channel in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement, all complete as per standard design : .30m deep with SFRC Cover and frame (heavy duty HD-20 grade designation) 560mm internal diameter conforming to I.S. 12592, total weight of cover and frame to be not less than 182 kg. fixed in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) including centering, shuttering all complete. (Excavation, foot rests and 12 mm thick cement plaster at the external surface shall be paid for separately) : With Sewer bricks conforming IS : 4885 | each | 4 |  |  | 0
53(a) | Extra depth for circular type manhole 1.52 m internal dia (at bottom) beyond 2.30 m : With Sewer bricks conforming IS : 4885 | m | 2 |  |  | 0
53 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS : 10910 on 12mm dia steel bar conforming to IS : 1786 having minimum cross section as 23 mmx25mm and over all minimum length 263 mm and width as 165mm with minimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture's permanent identification mark to be visible even after fixing, including fixing in manholes with 30x20x15 cm cement concrete block 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) complete as per design. | Nos | 390 |  |  | 0
54 | Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement and making necessary channels for the drain etc. complete :
(a) | For pipes 100 to 230 mm diameter | Nos | 48 |  |  | 0
Section - II: External Water Supply Works
55 | Providing and laying in trenches G.I. pipes medium class complete with G.I. fittings including excavation of trenches, refilling the same and testing of joints complete:
(a) | 20 mm dia nominal bore | Metre | 61 |  |  | 0
(b) | 40 mm dia nominal bore | Metre | 52 |  |  | 0
(c) | 50 mm dia nominal bore | Metre | 186 |  |  | 0
(d) | 80mm dia nominal bore | Metre | 23 |  |  | 0
(e ) | 100 mm dia nominal bore | Metre | 292 |  |  | 0
56 | Constructing brick masonry chamber for underground C.I. inspection chamber and bends with 75 class designation bricks in cement mortar 1:4 (1 cement : 4 coarse sand) M.S lockable cover of 6mm thk M>S plate with angle frame of 35x35x4 R.C.C. top slab with 1:2:4 mix (1 cement :2 coarse sand : 4 graded stone aggregate 20 mm nominal size) foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished smooth with a floating coat of neat cement on walls and bed concrete etc. complete as per standard design :
(a) | Inside dimensions 455x610 mm and 45 cm deep for single pipe line :
| With F.P.S. bricks | Each | 8 |  |  | 0
57 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end):
(a) | 50 mm nominal bore | each | 4 |  |  | 0
58 | Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete :
(a) | 20 mm nominal bore | each | 4 |  |  | 0
59 | Providing and fixing gun metal non- return valve of approved quality (screwed end) :
(a ) | 150 mm nominal bore | each | 10 |  |  | 0
60 | Supply and install test commissioning of horizontal split casing type centrifugal pump set with brass impellers capable of discharge water approx at 230 LPM at 25 MTR head directly coupled with suitable energy efficient induction motor 3 phase 415 V, 50 cycle mounted on MS channel common base plate and fixed with suitable bolts grouted in PCC foundation in PCC (1:2:4) type B1 using 20mm graded stone aggregate 30 cm above floor level including making connection of inlet and outlet with fitting including nut bolts, packing etc. and PVC insulated unsheathed copper conductor cable of suitable size multistranded in PVC conduit for connection from starter to motor with proper lugs of suitable size, pressure gauge of 0 to 10 kg/cm2 etc all as specified and directed.((1 working + 1 Standby) | Set | 1 |  |  | 0
Section - III: Irrigation and Gardening Works
61 | Providing and laying in trenches G.I. pipes medium class complete with G.I. fittings including excavation of trenches, refilling the same and testing of joints complete:
(a) | 25 mm dia nominal bore | Rm | 445 |  |  | 0
(b ) | 40 mm dia nominal bore | Rm | 248 |  |  | 0
(c) | 50 mm dia nominal bore | Rm | 45 |  |  | 0
(d) | 80 mm dia nominal bore | Rm | 694 |  |  | 0
62 | Constructing brick masonry chamber for underground C.I. inspection chamber and bends with 75 class designation FLAG bricks in cement mortar 1:4 (1 cement : 4 coarse sand) M.S lockable cover of 6mm thk M>S plate with angle frame of 35x35x4 R.C.C. top slab with 1:2:4 mix (1 cement :2 coarse sand : 4 graded stone aggregate 20 mm nominal size) foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished smooth with a floating coat of neat cement on walls and bed concrete etc. complete as per standard design :
(a) | Inside dimensions 300x300 mm for single pipe line : | Nos | 16 |  |  | 0
63 | Providing and fixing gun metal non- return valve of approved quality (screwed end) :
(a) | 80 mm nominal bore | Nos | 1 |  |  | 0
64 | Providing and fixing gun metalButter Fly valve of approved quality (screwed end)
(a) | 80 mm nominal bore | Nos | 6 |  |  | 0
(b ) | 50 mm nominal bore | Nos | 1 |  |  | 0
(C) | 40 mm nominal bore | Nos | 1 |  |  | 0
(d ) | 25 mm nominal bore | Nos | 8 |  |  | 0
65 | Providing and fixing Strainer of approved quality (screwed end) :
(a) | 100 mm nominal bore | Nos | 1 |  |  | 0
66 | Providing and fixing Water Meter of approved quality (screwed end) :
(a) | 100 mm nominal bore | Nos | 1 |  |  | 0
67 | Providing and fixing Water 80 cum sand filter duplex of 40 cum/hr,with semi automatic back wash option using hydraullic valves and accesorirs.: | Nos | 1 |  |  | 0
68 | Providing and fixing Pop up spray tupe 150 mm height having female connection | Nos | 42 |  |  | 0
69 | Supply and install test commissioning of horizontal split casing type centrifugal pump set with brass impellers capable of discharge water approx at 330 LPM at 25 MTR head directly coupled with suitable energy efficient induction motor 3 phase 415 V, 50 cycle mounted on MS channel common base plate and fixed with suitable bolts grouted in PCC foundation in PCC (1:2:4) type B1 using 20mm graded stone aggregate 30 cm above floor level including making connection of inlet and outlet with fitting including nut bolts, packing etc. and PVC insulated unsheathed copper conductor cable of suitable size multistranded in PVC conduit for connection from starter to motor with proper lugs of suitable size, pressure gauge of 0 to 10 kg/cm2 etc all as specified and directed. (1 working + 1 Standby) | Set | 1 |  |  | 0
Section -IV: Rain water Harvesting Works
70 | Construction of filter pit & boring for Rain water Harvesting of 150 mm with sloted UPVC pipe two nos in each filter pit all as per drawing and as directed etc complete for a depth of 10m. | NOS | 10 |  |  | 0
Section - V: Fire Fighting
71 | Supply, Installation, Testing & Commissioning of following sizes of G.I. pipes conforming to IS IS:1239 (heavy) with all accessories like all fittings (for pipes upto 50 mm dia standard threaded forged steel fittings and for pipes above 50 mm dia standard G.I. fitting with welded joint shall be used) requirement including cutting holes and chasses in brick, R.C.C. work and making good the same to original conditions complete including painting with one coat of zinccromate primer and two or more coats of synthetic enamel paint of approved make and shade complete in all respects. All hangers, clamps, brackets etc. shall be galvanised iron unless specified otherwise and then supply of the same shall also be included for rates under this head ( Fire sealent shall be provided to the contractor free of cost.)Riser pipeincluding tees, elbows reducers, union, flanges rubber gasket, G.I. nuts bolts, washer including g.i. supporting/fixing the pipe on floor/wall/ ceiling with clamps, hangers, (using anchor fastners) as per specification G.I. pipe sleeve of suitable higher size shall be provided wherever in the pipes are crossing the walls/floors and sealing the sleeves with glass wool in between and fire sealent compound at either and all as per Project Manager's.
(a) | 150 mm | Rm | 454 |  |  | 0
72 | Supplying and fixing single headed internal hydrant valve with instantaneous Gun metal couplings of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type - A) with blank Gunmetal cap and chain as required.
(a) | Included all internal hydrant valve (2 nos in internal FHC) | Nos | 16 |  |  | 0
73 | Supplying and fixing 63 mm dia, 15 mtr. long RRL hose pipe with 63 mm dia Male and Female Gun Metal couplings duly binded with GI wire, rivets etc. conforming to IS 636 (Type -A) as required.
(a) | Included in internal FHC ( 2nos for each internal FHC) | Nos | 32 |  |  | 0
74 | Supplying and fixing First-Aid Hose Reel with MS construction spray painted in Post office Red, cinforming to IS 884 with upto date amendments, complete with the following as required. 30 m. long 20 mm (nominal internal) dia water hose Thermoplastic (Textile 20 mm (nominal internal) dia gun metal Drum and brackets for fixing the equipmets on wall.
(a) | Included in all internal FHC (one each for FHC) | Nos | 16 |  |  | 0
75 | Supplying & fixing 63 mm dia Gun metal branch pipe with 20 mm (nominal internal diameter) size Gun Metal nozzle conforming to IS 903, suitable for instantaneous connection to interconnect hose pipe coupling as required.
(a) | Included in internal FHC ( 2nos for each internal FHC) | Nos | 16 |  |  | 0
76 | Supplying and fixing of hose cabinet of size 1000 mm x 2100 mm x 600 mm made of 2 mm thick MS sheet with 6 mm thick glazed glass doors i/c 'necessary locking arrangement suitable to accommodate external hydrant with butterfly valve, 2 Nos. 15 mtr. long Hose pipe, 1 No. branch pipe, mounted on wall OR raised brick platform & duly painted with Post office red externally and white internally with synthetic enamel paint complete in all respect, for external hydrant, as required.
(a) | Included inside the building (2NOs) | Nos | 16 |  |  | 0
77 | Providing, installation, testing and commissioning of dual plate non-return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc. as required.
(a) | 150mm dia | Nos | 1 |  |  | 0
78 | Supplying, fixing, testing and commissioning of butterfly valve PN 1.6, with Bronze/Gunmetal seat duly ISI marked complete with Nuts, Bolts, washers, gaskets, conforming to IS 13095 of following sizes as required.
(a) | 150 mm dia | Nos | 17 |  |  | 0
79 | Supply & Fixing ISI marked (IS:13849) Portable Fire Exitnguisher, ABC type capacity 5 kg, finished externally with red enamel paint, complete in all respects including initial fill and wall suspension. Capacity 5 kg | Nos | 22 |  |  | 0
80 | Supply & Fixing ISI marked (IS:2878) Portable fire Extinguisher, Carbon-dioxide type flat base including valve, discharge hose of not less than 10 mm dia. 1m long & complete in all respects including initial fill with C02 gas confirming to IS:307-1966 filled to a filling ratio of not more than 0.667of not more than 0.667and wall suspension bracket. Capacity 4.5 Kg | Nos | 22 |  |  | 0
81 | Supplying and fixing 2 Way FBC of CI body with 3 No. Gun Metal male instantaneous inlet couplings complete with cap and chain as required. For 100 mm dia M.S. Pipe connection conforming to IS : 904 as required. | Nos | 1 |  |  | 0
82 | Supplying and fixing air vessel made of 250 mm dia, 8 mm thick MS sheet,1200 mm. m height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia Gun metal wheel valve, with required accessories, pressure gauge and painting with synthetic enamel paint of approved shade as required. | Nos | 8 |  |  | 0
83 | S&F standard firemans axe with heavy rubber handle complete all as specified and directed. . | Nos | 16 |  |  | 0
84 | Supply, Fixing, Testing & Commissioning of elect fire pump (Main Pump for Down comer system) suitable for automatic operation consisting of following :Suitable delivery from 450 lpm & 50 m head (1W+IS) | Set | 1 |  |  | 0
SUB TOTAL OF PART B: PUBLIC HEALTH ENGINEERING AND FIRE FIGHTING WORKS | [5 empty] | 0

## P - C (Electrical)
BILL OF QUANTITY
PART C: ELECTRICAL WORKS
Sr. No. | Description of Items | Unit | Quantity | Rate In INR | Rate In Words | Amount In INR
INTERNAL ELECTRIFICATION
SECTION I - WIRING IN CONCEALED PVC CONDUIT
1 | Wiring for light/ fan/ exhuast fan/ call bell point with 1.5 sqmm FR PVC insulated stranded copper conductor single core cable in concealed PVC conduit, with 5 amp modular switch, modular base and cover plate, suitable size G.I. box and earthing the point with same size cable along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Short Point | Point | 651 |  |  | 0
b | Medium Point | Point | 1288 |  |  | 0
c | Long Point | Point | 2362 |  |  | 0
2 | Wiring for twin control light point with 1.5 sqmm FR PVC insulated stranded copper conductor single core cable in concealed PVC conduit, with 5 amp modular switch, modular base and cover plate, suitable size G.I. box and earthing the point with same size cable along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Point | 17 |  |  | 0
3 | Wiring for light plug point with 2 x 2.5 sq mm FR PVC insulated stranded copper conductor cable in concealed PVC conduit along with modular type 6 Amp switch and 3 pin 6 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size cable along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Short Point | Point | 477 |  |  | 0
b | Medium Point | Point | 943 |  |  | 0
c | Long Point | Point | 1727 |  |  | 0
4 | Wiring for power plug point with 2 x 4 sq mm FR PVC insulated stranded copper conductor cable in concealed PVC conduit along with modular type 16 Amp switch and 6 pin 16 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size cable along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Short Point | Point | 73.6 |  |  | 0
b | Medium Point | Point | 110.4 |  |  | 0
c | Long Point | Point | 184 |  |  | 0
5 | Wiring for power plug point with 2 x 6 sq mm FR PVC insulated stranded copper conductor cable in concealed PVC conduit along with modular type 32 Amp SP MCB "C" series and 6 pin 20 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size cablealong with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Short Point | Point | 34.2 |  |  | 0
b | Medium Point | Point | 51.3 |  |  | 0
c | Long Point | Point | 85.5 |  |  | 0
6 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in concealed PVC conduit along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 6 X 10 sq. mm in 40mm conduit | Meter | 600 |  |  | 0
b | 6 X 16 sq. mm in 50mm conduit | Meter | 100 |  |  | 0
c | 4 X 25 sq. mm + 2 X 16 sq. mm in 50mm conduit | Meter | 100 |  |  | 0
d | 4 X 35 sq. mm + 2 X 16 sq. mm in 50mm conduit | Meter | 10 |  |  | 0
7 | Supplying and fixing of following sizes PVC conduit along with accessories, hardwares etc in concealed as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 20 mm | Meter | 400 |  |  | 0
b | 25 mm | Meter | 200 |  |  | 0
c | 32 mm | Meter | 100 |  |  | 0
d | 40 mm | Meter | 100 |  |  | 0
e | 50 mm | Meter | 100 |  |  | 0
SECTION II - METAL, BOXES
8 | Supplying and fixing metal box of following sizes (nominal size) in recess with suitable size phenolic laminated sheet cover in front including painting along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 75 mm X 75 mm X 60 mm deep | Each | 500 |  |  | 0
b | 100 mm X 100 mm X 60 mm deep | Each | 100 |  |  | 0
c | 150 mm X 75 mm X 60 mm deep | Each | 150 |  |  | 0
d | 150 mm X 150 mm X 60 mm deep | Each | 50 |  |  | 0
e | 180 mm X 100 mm X 60 mm deep | Each | 50 |  |  | 0
f | 200 mm X 125 mm X 60 mm deep | Each | 20 |  |  | 0
g | 200 mm X 150 mm X 60 mm deep | Each | 10 |  |  | 0
h | 200 mm X 250 mm X 60 mm deep | Each | 10 |  |  | 0
i | 200 mm X 300 mm X 60 mm deep | Each | 10 |  |  | 0
SECTION III - SWITCHES & ACCESSORIES
9 | Supplying and fixing following modular switch, socket, other accessories on the existing modular plate & switch box including connections but excluding modular plate along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3 pin 5/6 amp socket outlet | Each | 50 |  |  | 0
b | 6 pin 15/16 amp socket outlet | Each | 50 |  |  | 0
c | 6 pin 20 amp socket outlet | Each | 50 |  |  | 0
10 | Providing and fixing composite unit for computer points having modular type 1 No 6 pin 16 amp socket outlet, 1 No 16 amp switch, 3 Nos 3 pin 6 amp socket outlets, 3 Nos 6 amp switches, suitable G.I. box, base and cover plates, earthing the sockets and switch box along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 2683 |  |  | 0
11 | Supplying and fixing call bell/ buzzer suitable for single phase, 230 volts A.C. supply, complete along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Deluxe | Each | 302 |  |  | 0
SECTION IV - FANS, LUMINARIES AND LAMPS
12 | Supplying, installation, testing and commissioning of following sizes ceiling fan with resistance type regulator, including wiring the down rods of standard length up to 30 cm with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable, earthing along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 1200 mm sweep | Each | 894 |  |  | 0
13 | Supplying and fixing following sizes of down rod of 15/20mm dia M.S. pipe of thickness 1.6mm to ceiling fan including painting with matching colour along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 45 cm long | Each | 894 |  |  | 0
14 | Providing and fixing round/ hexagonal fan box (125mm dia) depth 75mm (max.) with 12mm dia steel bar hook, 1.6mm thick MS sheet cover, in RCC slab along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 894 |  |  | 0
15 | Supplying, installation, testing and commissioning of following sizes fancy exhaust fan having built in louvers in existing opening in wall including earthing along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 225 mm sweep | Each | 80 |  |  | 0
b | 300 mm sweep | Each | 35 |  |  | 0
16 | Supplying, installation, testing and commissioning of following surface/ concealed type fluorescent fitting (luminaries) complete with copper ballast, glow type starter with fluorescent lamp, on ceiling/ wall surface, earthing the fitting along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 4' x 40 W single patti type (TCS019 1xTL-D36W ICO Philips or equivalent) | Each | 42 |  |  | 0
17 | Supplying, installation, testing and commissioning of following T-5 fluorescent fitting (luminaries) complete with electronic ballast but with fluorescent lamp, on ceiling/ wall surface, earthing the fitting along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Single mirror optic surface mounting type (FBS300 M 3xPL-L36W IC P5 Philips or equivalent) with lamp. | Each | 1035 |  |  | 0
18 | Supplying, installation, testing and commissioning of following mirror optics concealed type CFL fitting (luminaries) complete with copper ballast, but with CFL lamp, in false ceiling, earthing the fitting along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 1 x 36 W (TCS605 1xTL-D36W IC M1 Philips or equivalent) | Each | 42 |  |  | 0
b | 2 x 36 W (TCS605 2xTL-D36W IC M1 Philips or equivalent) | Each | 895 |  |  | 0
19 | Supplying, installation, testing and commissioning of following CFL down lighter luminaries with mirror reflector, but with CFL lamp, on surface/ recess in false ceiling including connection, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | For 1x13/18 watt CFL with cover (FBH145 M 1xPL-C/2P18W I 240V LH Philips or equivalent) | Each | 923 |  |  | 0
20 | Supplying, installation, testing and commissioning of following CFL down lighter luminaries with mirror reflector, with CFL lamp, on surface/ recess in false ceiling including connection, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | For Toilet - 1x18 watt CFL with cover (FBS075 1xPL-C/2P18W I 240V Philips or equivalent) | Each | 164 |  |  | 0
b | For Mirror Light - 1x11 watt CFL with cover (FBS100 1xPL-C/2P10W I 240V Philips or equivalent) | Each | 134 |  |  | 0
21 | Supplying, installation, testing and commissioning of following LED luminaries with mirror reflector, on surface/ recess in false ceiling including connection, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3W (IP20) LED - BBG360 1xLXML-25-/CW WH Philips or equivalent | Each | 360 |  |  | 0
22 | Supplying, fixing and testing of approved make bulk head luminaire (NXC101 1xA60-60W-CL B22 GR Philips or equivalent) consisting of pressure die cast Alu. Housing, lamp holder, prismatic glass cover, rubber gasket and wire guard delux type including fixing on wall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 46 |  |  | 0
23 | Supplying, installation, testing and commissioning of following 230/250 volts metal halide wide beam flood light luminaries with weather proof gear box, igniter, capacitor with IP 65 protection on wall surface/ building parapet/ pole bracket complete with lamp along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 1x250 watt (SRX051 1xSON250W Philips or equivalent) | Each | 60 |  |  | 0
24 | Numbering of ceiling fan/ exhaust fan/ fluorescent fittings along with accessories, hardwares etc as required for completeness and direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 5502 |  |  | 0
SECTION V - PANELS AND SMDB
25 | Design, manufacture, testing at works & supply of 2 mm thick MS sheet steel fabricated cubicle type Panel dust and vermin proof complete with hinged and lockable doors. All the panels shall be floor mounted and dead front construction complete with interconnections by copper tapes/ wires and painting. The Panels shall be provided with one no. of multifunction meter of EM6400 of Enercon make or equivalent along with associated C.T.'s & P.T.'s in the incoming feeder. The current density of the bus bar to be used in panel shall be 1.0 sq. mm/ amp for Cu. Bus Bar for aluminium bus bar 1.3 sq. mm/ amp. The panels along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | SMDB 1 GF (Location Electrical GF section 1) | Set | 1 |  |  | 0
Incoming:
315A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
315A, AL bus bar
Outgoing
63A MCB 10KA-2 nos
32A MCB 10KA-1 no
25A MCB 10KA-6 nos
16A MCB 10KA-3 nos
10A MCB 10KA-1 no
b | SMDB 2 GF (Location Electrical GF section 2) | Set | 1 |  |  | 0
Incoming:
250A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
250A, AL bus bar
Outgoing
32A MCB 10KA-1 no
25A MCB 10KA-7 nos
16A MCB 10KA-3 nos
c | SMDB 3 GF (Location Electrical GF section 3) | Set | 1 |  |  | 0
| Incoming: |  |  |  |  | 0
| 250A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM |  |  |  |  | 0
| Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse |  |  |  |  | 0
| Bus Bar |  |  |  |  | 0
| 250A, AL bus bar |  |  |  |  | 0
| Outgoing |  |  |  |  | 0
| 32A MCB 10KA-2 nos |  |  |  |  | 0
| 25A MCB 10KA-7 nos |  |  |  |  | 0
| 16A MCB 10KA-3 nos |  |  |  |  | 0
| 10A MCB 10KA-1 no |  |  |  |  | 0
d | SMDB 4 GF (Location Electrical GF section 4) | Set | 1 |  |  | 0
Incoming:
250A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
250A, AL bus bar
Outgoing
32A MCB 10KA-2 nos
25A MCB 10KA-7 nos
16A MCB 10KA-3 nos
10A MCB 10KA-2 nos
e | SMDB 1 FF (Location Electrical FF section 1) | Set | 1 |  |  | 0
Incoming:
630A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
630A, AL bus bar
Outgoing
160A MCCB 35KA-2 nos
63A MCB 10KA-4 nos
32A MCB 10KA-4 nos
25A MCB 10KA-4 nos
20A MCB 10KA-1 no
f | SMDB 2 FF (Location Electrical FF section 2) | Set | 1 |  |  | 0
Incoming:
630A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
630A, AL bus bar
Outgoing
100A MCCB 25KA-2 nos
80A MCCB 25KA-1 nos
63A MCB 10KA-5 nos
32A MCB 10KA-4 nos
25A MCB 10KA-2 nos
16A MCB 10KA-1 nos
g | SMDB 3 FF (Location Electrical FF section 3) | Set | 1 |  |  | 0
Incoming:
630A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
630A, AL bus bar
Outgoing
80A MCCB 25KA-2 nos
63A MCB 10KA-4 nos
32A MCB 10KA-8 nos
25A MCB 10KA-5 nos
h | SMDB 4 FF (Location Electrical FF section 4) | Set | 1 |  |  | 0
Incoming:
630A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
630A, AL bus bar
Outgoing
80A MCCB 25KA-2 nos
63A MCB 10KA-4 no
32A MCB 10KA-6 no
25A MCB 10KA-7 no
i | SMDB 5 TF (Location Electrical GF section4) FOR HVAC | Set | 1 |  |  | 0
Incoming:
1250A, 50 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
1250A, AL bus bar
Outgoing
1000A MCCB 50KA-2 nos
315 A MCCB 35KA-2 nos
25A MCB 10KA-1 no
j | SMDB OPEN THEATER | Set | 1 |  |  | 0
Incoming:
125A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
125A, AL bus bar
Outgoing
80A MCCB 25KA-2 nos
63A MCB 10KA-1 no
k | MCC PUMP | Set | 1 |  |  | 0
Incoming:
400A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
400A, AL bus bar
Outgoing
400A MCCB 35KA-2 nos
200A MCCB 35KA-1 no
l | MCC FIRE PUMP | Set | 1 |  |  | 0
Incoming:
125A, 25 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
150A, AL bus bar
Outgoing
63A MCB 10KA-2 nos
32A MCB 10KA-1 no
m | SMDB-TELECOM | Set | 1 |  |  | 0
Incoming:
125A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
150A, AL bus bar
Outgoing
63A MCB 10KA-2 nos
32A MCB 10KA-1 no
n | SMDB-EXTERNAL | Set | 1 |  |  | 0
Incoming:
125A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
150A, AL bus bar
Outgoing
63A MCB 10KA-2 nos
32A MCB 10KA-1 no
o | SMDB-MAST | Set | 1 |  |  | 0
Incoming:
200A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
200A, AL bus bar
Outgoing
200A MCCB 35KA-2 nos
125A MCCB 10KA-1 no
p | SMDB-SECURITY | Set | 1 |  |  | 0
Incoming:
160A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
160A, AL bus bar
Outgoing
125A MCCB 25KA-2 nos
63A MCB 10KA-1 no
q | SMDB-DORMETRY | Set | 1 |  |  | 0
Incoming:
125A, 35 KA, TP MCCB With Thermal Based O/L, S/C Release & ROM
Anolog Ammeter With Selector switch, Analog Voltmeter with Selector switch, CT-/5 A, 5VA, CL-1 For Metering, Indicating Lamps (R, Y, B, on/off/trip), Control Fuse
Bus Bar
80A, AL bus bar
Outgoing
80A MCCB 25KA-2 nos
32A MCB 10KA-1 no
SECTION VI - MAIN SWITCHES, MCCB’s, MCB’s & MCB DB’s
26 | Providing and fixing following rating and breaking capacity MCCB in existing cubicle panel board including drilling holes in cubicle panel, making connections along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 4 pole MCCB, 100A, 35KA | Each | 12 |  |  | 0
b | 4 pole MCCB, 200A, 35KA | Each | 3 |  |  | 0
c | 4 pole MCCB, 250A, 35KA | Each | 7 |  |  | 0
d | 4 pole MCCB, 400A, 35KA | Each | 8 |  |  | 0
e | 4 pole MCCB, 630A, 50KA | Each | 10 |  |  | 0
27 | Supplying and fixing on surface/ recess following way, 240 volts SP&N MCB distribution board of sheet steel phosphatized and powder painted complete with tinned copper busbar, neutral busbar, earth bar, din bar, detachable gland plate, including interconnections, earthing along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (But without MCB/ RCCB/ Isolator)
a | 4 way, Single door | Each | 4 |  |  | 0
b | 8 way, Single door | Each | 1 |  |  | 0
c | 12 way, Single door | Each | 57 |  |  | 0
28 | Supplying and fixing on surface/ recess horizontal type following way, 415 volts, TPN MCB distribution board of sheet steel phosphatized and powder painted, complete with tinned copper busbar, neutral busbar, earth bar, din bar, detachable gland plate, including interconnections, earthing along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (But without MCB/ RCCB/ Isolator)
a | 4 way Single door | Each | 16 |  |  | 0
b | 6 way Single door | Each | 8 |  |  | 0
c | 8 way Single door | Each | 37 |  |  | 0
29 | Supplying and fixing DP MCB, 240 volts, 'C' series, suitable for inductive/ motor load in the existing MCB DB complete with connections, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 0.5 amps to 5 amps | Each | 20 |  |  | 0
b | 6 amps to 32 amps | Each | 596 |  |  | 0
c | 40 amps | Each | 200 |  |  | 0
30 | Supplying and fixing TP&N MCB, 440 volts, 'C'series, suitable for inductive/ motor load in the existing MCB DB complete with connections, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 0.5 amps to 5 amps | Each | 20 |  |  | 0
b | 6 amps to 32 amps | Each | 982 |  |  | 0
c | 40 amps | Each | 100 |  |  | 0
d | 50 amps | Each | 50 |  |  | 0
e | 63 amps | Each | 100 |  |  | 0
30 (a) | Supplying and fixing following rating, double pole, (single phase and neutral), 240 volts, residual current circuit breaker (RCCB), having a sensitivity current up to 300 milliamperes in the existing MCB DB complete with connections, testing and commissioning etc. as required
a | 25 amps | Each | 52 |  |  | 0
b | 40 amps | Each | 25 |  |  | 0
c | 63 amps | Each | 282 |  |  | 0
31 | Supplying and fixing following rating, 240 volts TWO POLE ISOLATOR in the existing MCB DB complete with connections, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 40 amps | Each | 15 |  |  | 0
b | 63 amps | Each | 20 |  |  | 0
c | 100 amps | Each | 4 |  |  | 0
32 | Supplying and fixing following rating, 415 volts, FOUR POLES, ISOLATOR in the existing MCB DB complete with connections, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 40 amps | Each | 5 |  |  | 0
b | 63 amps | Each | 10 |  |  | 0
c | 100 amps | Each | 2 |  |  | 0
33 | Supplying and fixing 2 pole and earth, 240 volts, industrial type, socket outlet, enclosed metal plug top along with SP MCB in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 20 Amp with “C” series MCB | Each | 6 |  |  | 0
b | 32 Amp with “C” series MCB | Each | 4 |  |  | 0
34 | Supplying and fixing TPN and earth, 440 volts, industrial type, socket outlet, enclosed metal plug top along with MCB, in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket out let and complete with connections, testing and commissioning along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 20 Amp with “C” series TP MCB | Each | 6 |  |  | 0
b | 32 Amp with “C” series TP MCB | Each | 4 |  |  | 0
SECTION VII - UPS, INVERTORS
35 | Supplying, installation, testing and commissioning following rating single phase, 230 volts offline UPS with seperate battery including connection along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (With 15 Minute Backup)
a | 1.00 KVA | Each | 9 |  |  | 0
36 | Supplying, installation, testing and commissioning following rating three phase, 40 kVA online UPS with seperate battery including connection along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (With 15 Minute Backup)
a | 40 KVA | Each | 10 |  |  | 0
37 | Supplying, installation, testing and commissioning following rating lead acid battery including connection along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 45 AH | Each | 9 |  |  | 0
b | 120 AH | Each | 10 |  |  | 0
SECTION VIII - EARTHING
PLATE EARTH ELECTRODE
38 | Earthing with G.I. earth plate 600 mm X 600 mm X 6 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Set | 54 |  |  | 0
39 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Set | 14 |  |  | 0
COPPER WIRE/ STRIP CONNECTION
40 | Providing and fixing 25 mm X 5 mm copper strip in 40 mm dia G.I. pipe from earth electrode at 0.5 Metre depth below ground level including excavation and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 280 |  |  | 0
41 | Providing and fixing 25 mm X 5 mm copper strip on surface or in recess for connections along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 50 |  |  | 0
42 | Supplying and laying 25 mm X 6 mm G.I. strip at 0.50 Meter below ground as strip earth electrode, including soldering, excavation and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 1080 |  |  | 0
43 | Providing and fixing 25 mm X 5 mm G.I. strip in 40 mm dia G.I. pipe from earth electrode at 0.5 Metre depth below ground level including excavation and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 540 |  |  | 0
44 | Providing and laying earth connection from earth electrode with 6 SWG dia G.I. Wire in 15 mm dia G.I. pipe from earth electrode at 0.5 Metre depth below ground level including excavation and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 3000 |  |  | 0
45 | Providing and fixing 25 mm X 5 mm G.I. strip on surface or in recess for connections along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 400 |  |  | 0
46 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 2000 |  |  | 0
47 | Providing and fixing 6 SWG dia G.I. wire on surface or in recess for loop earthing along with existing surface/ concealed conduit/ submain wiring/ cable along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Meter | 500 |  |  | 0
SECTION IX - LIGHTNING CONDUCTOR
G.I. FINIAL/ G.I. CONNECTION
48 | Providing and fixing of lightning conductor finial, made of 25 mm dia 300 mm long, G.I. tube, having single prong at top, with 85 mm dia 6 mm thick G.I. base plate having 4 nos holes for fixing etc. complete along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 6 |  |  | 0
49 | Making jointing of G.I. tape (with another G I tape, base of the finial or any other metallic object) by reverting, sweating and soldering/ nut bolting along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 200 |  |  | 0
50 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (For horizontal run) | Metre | 2400 |  |  | 0
51 | Providing and fixing G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (For vertical run) | Metre | 720 |  |  | 0
52 | Providing and fixing testing joint, made of 20 mm X 3 mm thick G.I. strip, 125 mm long, with 4 nos. of G.I. bolts, nuts, chuck nuts and spring washers along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 20 |  |  | 0
53 | Providing and laying G.I. tape 32 mm X 6 mm from earth electrode directly in ground along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Metre | 480 |  |  | 0
54 | Fixing of lightning conductor finial, made of 25 mm dia 300mm long, copper tube/ G.I. tube, having single prong at top, with 85 mm dia 3mm thick copper base plate including holes along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 6 |  |  | 0
55 | Fixing of copper/ G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (For horizontal run) | Metre | 2400 |  |  | 0
56 | Fixing of copper/ G.I. tape 20 mm X 3 mm thick on parapet or surface of wall for lightning conductor along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (For vertical run) | Metre | 720 |  |  | 0
57 | Laying copper/ G.I. tape 32 mm X 6 mm from earth electrode directly in ground along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Metre | 480 |  |  | 0
SECTION X - HDPE, G.I. & RCC PIPES
58 | Supplying and laying double wall HDPE pipe having corrugation on the outer wall and plan surface on inner wall in ground below road, path etc at a depth not less than 40 cm including excavation, dismantling of road if required and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 90 mm outer dia | Metre | 250 |  |  | 0
b | 110 mm outer dia | Metre | 250 |  |  | 0
c | 150 mm outer dia | Metre | 100 |  |  | 0
d | 200 mm outer dia | Metre | 300 |  |  | 0
SECTION XI - MV CABLE LAYING AND BUS DUCT
59 | Supplying and laying following sizes one number PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade direct in ground including excavation, sand cushioning, protective covering and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3.5 x 25 sq. mm. | Meter | 200 |  |  | 0
b | 3.5 x 35 sq. mm. | Meter | 100 |  |  | 0
c | 3.5 x 50 sq. mm. | Meter | 400 |  |  | 0
d | 3.5 x 70 sq. mm. | Meter | 160 |  |  | 0
e | 3.5 x 95 sq. mm. | Meter | 100 |  |  | 0
f | 3.5 x 120sq. mm. | Meter | 794 |  |  | 0
g | 3.5 x 185 sq. mm. | Meter | 100 |  |  | 0
h | 3.5 x 300 sq. mm. | Meter | 7000 |  |  | 0
60 | Supplying and laying following sizes additional one number, PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade direct in ground as in the same trench in one tier horizontal formation including excavation, sand cushioning, protective covering and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3.5 x 25 sq. mm. | Meter | 25 |  |  | 0
b | 3.5 x 35 sq. mm. | Meter | 10 |  |  | 0
c | 3.5 x 50 sq. mm. | Meter | 40 |  |  | 0
d | 3.5 x 70 sq. mm. | Meter | 5 |  |  | 0
e | 3.5 x 95 sq. mm. | Meter | 5 |  |  | 0
f | 3.5 x 120sq. mm. | Meter | 10 |  |  | 0
g | 3.5 x 185 sq. mm. | Meter | 10 |  |  | 0
h | 3.5 x 300 sq. mm. | Meter | 2268 |  |  | 0
61 | Supplying and making end termination with brass compression gland and aluminum lugs for following size armoured aluminum conductor power cable of 1.1 KV grade along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3½ X 25 sq. mm | Each | 2 |  |  | 0
b | 3½ X 35 sq. mm | Each | 2 |  |  | 0
c | 3½ X 50 sq. mm | Each | 2 |  |  | 0
d | 3.5 x 70 sq. mm. | Each | 2 |  |  | 0
e | 3.5 x 95 sq. mm. | Each | 2 |  |  | 0
f | 3.5 x 120sq. mm. | Each | 2 |  |  | 0
g | 3.5 x 185 sq. mm. | Each | 2 |  |  | 0
h | 3½ X 300 sq. mm | Each | 116 |  |  | 0
62 | Supplying and making outdoor end termination with cast resin compound including aluminum lugs and other jointing materials for following size of PVC insulated and PVC sheathed/ XLPE aluminum conductor power cable of 1.1 KV grade along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3½ X 35 sq. mm | Each | 2 |  |  | 0
b | 3½ X 50 sq. mm | Each | 2 |  |  | 0
c | 3.5 x 70 sq. mm. | Each | 2 |  |  | 0
d | 3.5 x 95 sq. mm. | Each | 2 |  |  | 0
e | 3½ X 300 sq. mm | Each | 4 |  |  | 0
63 | Supplying and making straight through joint with heat shrinkable joint kit including aluminium ferrules for following size of PVC insulated and PVC sheathed/ XLPE aluminum conductor cable of 1.1 KV grade along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3½ X 25 sq. mm | Each | 4 |  |  | 0
b | 3½ X 35 sq. mm | Each | 4 |  |  | 0
c | 3½ X 50 sq. mm | Each | 4 |  |  | 0
d | 3½ X 70 sq. mm | Each | 4 |  |  | 0
e | 3½ X 95 sq. mm | Each | 4 |  |  | 0
f | 3½ X 120 sq. mm | Each | 4 |  |  | 0
g | 3½ X 185 sq. mm | Each | 4 |  |  | 0
h | 3½ X 300 sq. mm | Each | 6 |  |  | 0
SECTION XII - CABLE TRAYS AND ROUTE MARKER
64 | Supplying and installing following size powder coated, perforated M.S. cable trays with perforation not more than 17.5% rigidly suspended from the ceiling with M.S. suspenders at a distance not more than 2.5 metre and near every junction/ joint along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 150 mm width x 50 mm depth x 1.6 mm thickness | Meter | 610 |  |  | 0
b | 300 mm width x 50 mm depth x 1.6 mm thickness | Meter | 610 |  |  | 0
c | 450 mm width x 50 mm depth x 2.0 mm thickness | Meter | 610 |  |  | 0
65 | Supplying and fixing of following sizes powder coated, perforated, M.S. cable trays bends (horizontal) turning at 900 in same plane with perforation not more than 17.5% rigidly jointed with cable tray along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 150 mm width x 50 mm depth x 1.6 mm thickness | Each | 30 |  |  | 0
b | 300 mm width x 50 mm depth x 1.6 mm thickness | Each | 30 |  |  | 0
c | 450 mm width x 50 mm depth x 2.0 mm thickness | Each | 30 |  |  | 0
66 | Supplying and fixing of following sizes vertical, powder coated, perforated, M.S. cable trays bends (vertical) turning at 900 in another plane with perforation not more than 17.5% rigidly jointed with cable tray along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 150 mm width x 50 mm depth x 1.6 mm thickness | Each | 30 |  |  | 0
b | 300 mm width x 50 mm depth x 1.6 mm thickness | Each | 30 |  |  | 0
c | 450 mm width x 50 mm depth x 2.0 mm thickness | Each | 30 |  |  | 0
67 | Supply, installation, testing and commissioning (including if required cutting of finish floor) of under floor with standard thickness of 1.6 mm and depth of 48 mm. (The raceway shall be complete with all accessory reqd such as bends, tees, reducers, offsets, cover, junction boxes, suitable clamps, dash fasteners, cable ties, gaskets etc. as reqd.All raceways are to be cleaned thoroughly before pulling any wire/cable. Including earthing of trunking with 4 Sq mm PVC insulated Yellow + Green copper earth wire with proper thimbles). The floor along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 250mm x 50mm (1 Compartment) including joint sleeves. | RM | 1578 |  |  | 0
b | 150mm x50mm (1 Compartment) including joint sleeves. | RM | 1578 |  |  | 0
c | 100mm x 50mm (1 Compartment) including joint sleeves. | RM | 1184 |  |  | 0
d | 50mm x 50mm (1 Compartment) including joint sleeves. | RM | 3551 |  |  | 0
SECTION XIII - POLE AND POLE ERECTION
68 | Supply of hot dipped galvanized (in single dip to average 70 micron) octoganal pole made of 4mm thick steel plate having base plate 240 x 240 x 16mm, window and flush cover with locking arrangement at suitable height from base for cable termination block, pole suitably reinforced with welded steel section at window cut section to make the strength of pole unaffected, including template and anchor plate 240 x 240 x 3mm with 4 nos 700mm long, 20mm dia foundation bolts (EN8 grade) along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 8 metre high, minimum dia 162mm at bottom and 75mm at top | Each | 60 |  |  | 0
69 | Supply and fixing following street light pole bracket on existing pole made out of 50 mm dia MS "B" class pipe welded to 300 mm long MS pole canopy of suitable dia at a angle of 102.50 including having MS triangular stiffner of size 150 x 50 x 5 mm thick, making arrangement for tightening the bracket with pole by providing suitable size heavy duty nuts and bolts in canopy, painting with one coat of approved steel primer along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Single Over Hang 1.00 metre Long | Each | 60 |  |  | 0
70 | Erection of GI octogonal pole on existing cement concrete foundation having grouted bolts and nuts, aligning in true vertical position along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 8 metre high | Each | 60 |  |  | 0
71 | Supplying and fixing water tight terminal box made of 1.6mm thick M.S. sheet with detachable gland plate in bottom, hinged front open able cover, rubber gasket, having 2 Nos 4way connector and 1 No SPMCB inside the box for cable connection, fixed to pole with 2 Nos clamp made from 40 x 3mm M.S. flat with 2 No nut bolt dully painted with 2 coat of red oxide paint and 2 coat aluminium paint along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 60 |  |  | 0
72 | Supplying and drawing following sizes of FR PVC insulated copper conductor, single core cable in the existing surface/ concealed, steel/ PVC conduit/ PVC casing caping along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 2X2.5sqmm | meter | 600 |  |  | 0
73 | Designing and providing suitable RCC foundation for 3mere to 12 metre high GI octagonal pole including steel reinforcement (minimum 90kg per cum), form work, embeding 2 nos 50mm dia PVC pipe for cable entry in each foundation, excavation disposal of surplus soil and curing along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | CUM | 30 |  |  | 0
SECTION XIV - LIFT
74 | Suppy, installation, testing & commissitioning and putting into operation and final testing of automatic lift complete with all standard equipments, accessories and control equipments as per manufacturer's design and as per CPWD specification (Part III LIFTS) 1981and fulfilling following requirments on turn key basis. A. Type: Passenger lift | Job | 2 |  |  | 0
B. Load: 8 passenger/ 544 Kg
C. Speed: 1.0 metre per second
D. Contol: AC2
E. Operation: Microprosser based simplex collective selective with/without lift attendent
F. Total rise: About 9 mtrs
G. Landings: 2 All on same side
H. Floors served: G+1
I. Signals: Digital car position indicator, car travel direction indicator in car & at all landings
J. Lift shaft size: About 1800 mm width X 1760 mm depth, finished with plaster
K. Lift car size: About 1400 mm width X 1200 mm depth
L. Car entrance: Clear opening 800 mm wide X 2000 mm high protected with car door
M. Landing entrance: Clear opening 800 mm wide X 2000 mm high protected with landing door
N. Car door: Stainless steel two pannel centre opening flush type
O. Landing door: Mild steel two pannel centre opening flush type P. Door operation: Automatic electric power operated door with infra red protection
Q. Car interior: Stainless steel pannel with hair line finish on all sides
R. Car floor: Hard wood covered with PVC/ marblex tiles
S. Car ceiling & lighting: Fluorscent lighting concealed by suspended false ceiling with plain acrylic diffuser. The frame of suspended false ceiling shall be of powder coated aluminium
T. Car ventilation: Pressure fan with anodised aluminium grill
U. Emergency lighting in car: Battery operated Emergency lighting in the lift car
V. Intercom system: Battery operated Intercom system in lift car, machine room and control room
W. Emergency alarm: Battery operated alarm bell system in lift car & contol room
X. Position of machine room: Directly above the lift shaft
Y. Electric power supply: AC 415 Volts 3 phase 50 Hz terminated in machine room
Z. Fire man switch: Fire man switch at main landing terminal
SECTION XV - EAPBX, TV and LAN System
75 | Supplying and fixing of following sizes PVC conduit along with accessories in concealed along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (EAPBX+LAN+TV )
a | 20 mm | Rm | 37160.1 |  |  | 0
b | 25 mm | Rm | 45417.9 |  |  | 0
76 | Supplying and fixing following modular switch, socket, other accessories on the existing modular plate & switch box including connections but excluding modular plate along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | Telephone Socket outlet (RJ - 11) | Nos | 2748.2 |  |  | 0
b | TV Antenna socket outlet | Nos | 74 |  |  | 0
c | Computer outlet Jack ( RJ-45) | Nos | 2683 |  |  | 0
76 (i) | Supply and fixing of co-axial cable (RG-11) from Splitter box to main Tag Block at Basement, including saddles, clamps etc. complete as required. (Cable shall be 2 layer shielded). | Rm | 1850 |  |  | 0
76 (ii) | Supply & laying of RG-6 cable from Splitter box to points inside the Apartments in existing conduits. (Cable shall be 2 layer shielded). | Rm | 1110 |  |  | 0
76 (iii) | Supply and drawing of cat 6 Data cable in existing conduit complete as required. | Rm | 40245 |  |  | 0
77 | Supplying and fixing following size/ modules, GI box along with modular base & cover plate for modular switches in recess along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
(a) | 2 Module (75mm x 75mm) | Nos | 2752.6 |  |  | 0
77 (i) | Supplying and drawing the following sizes of anealed tinned electrolytic copper conductor PVC insulated unshielded twisted telephone wires in existing conduit and making connection on both the ends.
(a) | 2 pair ( 0.61 mm) | Rm | 41223 |  |  | 0
78 | Supply, installation and commissioning of IP Converged (Internet Protocol) Based Electronic Automatic Private exchange System (EAPBX) with SM (Switch Mode) dual power supply for redundancy having all cards Hot Swappable, wired for 1000 Ports and Expandable upto 1200 ports and with all features as per Additional Technical Specifications along with Hardware for 1000 Analog extensions, 100 IP Phones' Interface, 200 Channels SIP Trunking Hardware (For integration with Nursing College and Medical College Systems), Analog Trunk Lines Interface-48 Nos, 4 No ISDN PRI Interface (30 Channels) along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos | 1 |  |  | 0
79 | Supply and fixing of 10 pair telephone junction Box Suitable for 2 pair telephone wire along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (krone Make or equivalent). | Nos | 274.82 |  |  | 0
80 | Supply & drawing including termination of RG-6 cable for TV in existing conduit along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos | 148 |  |  | 0
81 | Supply and fixing in position of TV Splitter along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (2 Way) | Nos | 50 |  |  | 0
SECTION XVI - CCTV
82 | Supplying and fixing of 20mm steel conduit along with accessories in surface/ recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Rm | 1440 |  |  | 0
83 | Supplying and fixing of 25mm steel conduit along with accessories in surface/ recess including painting in case of surface conduit, or cutting the wall and making good the same in case of recessed conduit along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Rm | 960 |  |  | 0
SECTION XVII - FIRE ALARM SYSTEM
84 | Supply, installation, testing and commissioning of UL listed Photo thermal multicriteria intelligent addressable detector with standard base along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 890 |  |  | 0
85 | Supply, installation, testing and commissioning of Addressable rate of rise cum fixed temperature thermistor type resettable heat detector LED along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 100 |  |  | 0
86 | Supply, installation, testing and commissioning of Addressable MULTITECH HIGH SENSITIVITY detectors for server rooms with LED along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 6 |  |  | 0
87 | Supply, installation, testing and commissioning of UL listed LED type Response Indicator along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 50 |  |  | 0
88 | Supply, installation, testing and commissioning of manual push button to initiate audio alarm with a breakable glass cover/ resettable, intelligent addressable type along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 10 |  |  | 0
89 | Supply, installation, testing and commissioning of Fire Alarm Hooter, intelligent, addressable, (sound output of minimum 90 dB upto a distance of 30 meters) with strobe light of 110 cd intensity with power supply arrangement along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards and suitable for wall/ceiling mounting and as per specifications. Colour of hooter to be approved by architect before placing the order. | Nos. | 30 |  |  | 0
90 | Supply, installation, testing and commissioning of addressable monitor module along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 20 |  |  | 0
91 | Supply, installation, testing and commissioning of addressable control module complete as required for switching ON of smoke extraction fans/ Pressurisation Fans etc. and switching off AHU' s complete as required and as per specifications. | Nos. | 20 |  |  | 0
92 | Supply, installation, testing and commissioning of micro processor based 12 zone fault tolerant loop, required loop networkable type (each loop accessing minimum 125 detectors and 125 modules) fire alarm/ detection control panel. The panel shall be able to give location of all fire/ fault conditions of addressable units via the address codes. Further, the panel must be able to automatically switch ON/OFF respective control module when ever any alarm is triggered. The panel shall have rectifier, Loop cards, LCD unit to indicate Fire/ Fault Signal with address and analog output, external/ inbuilt printer to log all fire or fault events complete in all respects. The panel shall have a built in power supply and battery charger along with maintenance free 24 AH, 2 x 12 volt SMF Lead acid batteries capable of running for a minimum of 8 hours with battery charger complete as required and as per specifications. The panel shall have auto voice dialing facility for 6 telephone nos. The panel shall have a facility to relay a pre- recorded message to the PA system. The Panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 1 |  |  | 0
EXTERNAL ELECTRIFICATION
SECTION I - 33 KV H.T. Panel
93 | Five section HT panels inside the Receiving substation: Supplying, Erection, Testing and Commissioning of 33 KV extensible type Panel Board suitable for indoor installation for use on 33 KV 50 c/s earthed system having a symmertrical breaking capacity of 630 MVA for 1 Sec. at 33 KV comprising. The panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Set | 1 |  |  | 0
INCOMING
33KV, 630A, 1500MVA 2.5MM CRCA 1NO
ENCLOSURE WITH COPPER BUSBAR BOTH 1 NO
HORIZONTAL AND VERTICAL RUNS,
CONTROL WIRING & MISCELLANOUS ITEM
2.5MM CRCA INDOOR ENCLOSURE
DOOR SYSTEM
CIRCUIT BREAKER
33KV, 630A, 1500MVA VCB WITH RKG HANDLE 1 NO
CONTROL VOLTAGE: 230VAC
AUX VOLTAGE: 24 V DC
CURRENT TRANSFORMER
CAST RESIN CT’S OF RATIO ---/5/5A 1 NO
CL 1.0 / 5P10, 15 VA
POTENTIAL TRANSFORMER
CAST RESIN PT’S OF RATIO 1 NO
33KV/110V, CL 1.0, 100VA
√ 3 √3
MISCELLANOUS
HOOTER/ BUZZER 1 NO
2 POLE, 25A SPRING RETURN TO NEUTRAL - BCS 1 NO
LOCAL/ REMOTE SWITCH - 6A, 2 WAY 1 NO
SPACE HEATER - 100W 1 NO
THERMOSTAT - 30 TO 110*c 1 NO
EMERGENCY PUSH BOTTON 1 NO
24V DC POWER PACK 1 NO
CONTROL MCB
DOUBLE POLE, 10KA, 6A 3 NO
SINGLE POLE, 10KA, 6A 5 NO
SINGLE POLE, 10KA, 10A 2 NO
LED
RED INDICATING LAMP 2 NO
YELLOW INDICATING LAMP 2 NO
BLUE INDICATING LAMP 2 NO
GREEN INDICATING LAMP 1 NO
CLEAR INDICATING LAMP 1 NO
ORANGE INDICATING LAMP 1 NO
METERS
DIGITAL MULTIFUNCTION METER (EM6400) CL 1.0 WITH RS 485 PORT 1 NO
RELAY-CTR 5A, AUX.24V DC
AUX RELAY FOR ANTIPUMPING - 10A, 2NO+2NC 1 NO
NUMERICAL IDMT RELAY WITH O/C & E/F ELEMENT 1 NO
HIGH SPEED TRIPPING RELAY 1 NO
OUTGOING PANEL
33KV, 630A, 1500MVA 2.5MM CRCA 3 NO
ENCLOSURE WITH COPPER BUSBAR BOTH 1 NO
HORIZONTAL AND VERTICAL RUNS,
CONTROL WIRING & MISCELLANOUS ITEM
2.5MM CRCA INDOOR ENCLOSURE
DOOR SYSTEM
CIRCUIT BREAKER
33KV, 630A, 1500MVA VCB WITH RKG HANDLE 3 NO
CONTROL VOLTAGE: 230VAC
AUX VOLTAGE: 24 V DC
CURRENT TRANSFORMER
CAST RESIN CT’S OF RATIO ---/5/5A 3 NO
CL 1.0 / 5P10, 20 VA
MISCELLANOUS
HOOTER/ BUZZER 1 NO
2 POLE, 25A SPRING RETURN TO NEUTRAL - BCS 3 NO
LOCAL/ REMOTE SWITCH - 6A, 2 WAY 3 NO
SPACE HEATER - 100W 1 NO
THERMOSTAT - 30 TO 1100c 1 NO
EMERGENCY PUSH BOTTON 1 NO
8 WINDOW ANNUNCIATOR 1NO
CONTROL MCB
DOUBLE POLE, 10KA, 6A 3 NO
SINGLE POLE, 10KA, 6A 5 NO
SINGLE POLE, 10KA, 10A 3 NO
LED
RED INDICATING LAMP 2 NO
YELLOW INDICATING LAMP 2 NO
BLUE INDICATING LAMP 2 NO
GREEN INDICATING LAMP 1 NO
CLEAR INDICATING LAMP 1 NO
ORANGE INDICATING LAMP 1 NO
METERS
DIGITAL VAF METER (DM6100) CL 1.0 1 NO
RELAY-CTR 5A, AUX. 24V DC
AUX RELAY FOR ANTIPUMPING - 10A, 2NO+2NC 1 NO
AUX RELAY 8 NO
NUMERICAL IDMT RELAY WITH O/C & E/F ELEMENT 1 NO
HIGH SPEED TRIPPING RELAY 1 NO
SECTION II - TRANSFORMERS
94 | Supplying, Erection, Testing and Commissioning of 1250 KVA copper wound 33 KV/415 Volts, 50 C/S, Delta/Star DYn-11 connected Oil Type Transformer with off-load circuit tap changer minus 10% to plus 5% on H.T. side in steps of 2.5% complete with all accessories as per specifications including S/F of M.S. channel including connections along with accessories, hardwares etc as required for completeness and as per attached specification & drawing, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos | 3 |  |  | 0
SECTION III - HT Cables
95 | Supplying and laying one number following sizes XLPE, steel armoured, aluminium conductor power cable of 33 KV grade direct in ground including excavation, sand cushioning, protective covering and refilling the trench along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 3 x 240 sqmm | Rm | 600 |  |  | 0
96 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminum conductor cable of 33 KV grade along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 240 sq. mm | Each | 6 |  |  | 0
97 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminum conductor cable of 33 KV grade along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 240 sq. mm | Each | 22 |  |  | 0
98 | Supplying and making straight through cable jointing with heat shrinkable jointing kit complete with all accessories including ferrules suitable for following size of 3 core, XLPE aluminum conductor cable of 33 KV grade along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards.
a | 240 SQ. mm | Each | 6 |  |  | 0
SECTION IV - LT Panel, CAPACITOR Panel & PLC Panel
99 | Supply erection, testing and comiissioning of LT Panel fully compatmentalized cubical type sheet steel clad floor mounted totally enclosed extensible on both sides switch board suitable for use on 430 V, 3 phase 4 wire 50 c/s System having 50 KA fault capacity, housed with incoming and outgoing aluminium bus bars interconnection etc. with indication lmps, accessories etc. as required and complete with following incoming and outgoing switchgears with protection and metering etc. as per specification and schematic diagram complete as required. The panel shall be compatible with PLC/PC. LT PANEL WITHOUT CAPACITOR BANK. The Panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Set | 1 |  |  | 0
a | INCOMER: 3 NOS. DG SET (CABLE CONNECTION)
2000A 4P EDO ACB (50kA) with Microprocessor Based Release for O/C, S/C (MICROLOGIC 2.0A) 3 NOS
Indicating Lamps sets 3 nos
Digital Multi Function Meter, CL-1.0 (EM6400) With RS 485 Port 9 nos
CT's 2000/5A, 15VA, CL-1.0 for Metering 6 nos
2A SP Control MCB, 10kA 3 nos
INCOMER: 3 NOS. Transformer (CABLE CONNECTION)
2000A 4P EDO ACB (50kA) with Microprocessor Based Release for O/C, S/C (MICROLOGIC 2.0A) 3 NOS
Breaker Control Switch 3 nos
Digital Multifunction Meter, CL-1.0 (EM6400) With RS 485 Port 3 nos
CT's 2000/5A, 15VA, CL-1.0 for Metering 3 nos
CT's 2000/5A, 15VA, CL-5P10 for Protection 9 nos
CT's 2000/5A, 15VA, CL-Ps for Protection 18 nos
IDMT Relay 3 nos
Under/Over Voltage Relay 6 nos
REF 3nos
Auto/ Manual Selector Switch 3 nos
Auxillary Contactors 3 sets
Indicating Lamps - R,Y,B & ON/OFF/Trip 3 sets
2A SP Control MCB, 10kA 3sets
BUS COUPLER 1, 2: (DUCT CONNECTION)
2000A FP EDO ACB (50kA) without release. 3 nos
Breaker Control Switch 3 nos
Auxillary Contactors 3 nos
ON Delay Timer 3 nos
Indicating Lamps - ON/OFF/Trip 3 nos
2A SP Control MCB, 10kA 3 nos
Mech/ Electrical Interlocking 1 sets
OUTGOINGS: CABLE CONNECTION
1250A 4P MDO ACB (65kA) with Microprocessor Based Release for O/C, S/C & E/F Release 1 nos
1000A 4P MDO ACB (65kA) with Microprocessor Based Release for O/C, S/C & E/F Release 2 nos
800A 4P MCCB (50kA) with Microprocessor Based Release for O/C, S/C (MICROLOGIC 2.0A) and ROM 3 nos
630A 4P MCCB (50kA) with Microprocessor Based Release for O/C, S/C and ROM 5 nos
450A 4P MCCB (50kA) with Microprocessor Based Release for O/C, S/C and ROM 6 nos
315A 4P MCCB (50kA) with Microprocessor Based Release for O/C, S/C and ROM 1 nos
250A 4P MCCB (50kA) with Microprocessor Based Release for O/C, S/C and ROM 3 nos
200A 4P MCCB (50kA) with Thermal Magnetic Based Release for O/C, S/C and ROM 1 nos
125A 4P MCCB (35kA) with Thermal Magnetic Based Release for O/C, S/C and ROM 4 nos
63A 4P MCCB (25kA) with Thermal Magnetic Based Release for O/C, S/C and ROM 2 nos
Indicating Lamps 28 sets
AMMETER WITH SLECTOR SWITCH 28 nos
CT's 1250/5A, 15VA, CL-1.0 for Metering 1 nos
CT's 1000/5A, 15VA, CL-1.0 for Metering 2 nos
CT's 800/5A, 15VA, CL-1.0 for Metering 3 nos
CT's 630/5A, 15VA, CL-1.0 for Metering 5 nos
CT's 450/5A, 15VA, CL-1.0 for Metering 6 nos
CT's 300/5A, 15VA, CL-1.0 for Metering 4 nos
CT's 200/5A, 15VA, CL-1.0 for Metering 1 nos
CT's 125/5A, 15VA, CL-1.0 for Metering 4 nos
CT's 60/40A, 15VA, CL-1.0 for Metering 2 nos
2A SP Control MCB, 10kA 28 sets
100 | Suppling, installation, testing and commissioning of cubical type CRCA sheet steel standing free indoor type 400 KVAR fully automatic capacitor panel with dielectric self healing type shunt capacitor 7% D-tuned harmonic filte with current limiting device discharge register and with 1000A TPN aluminium bus bars and accessories with connections. The panel shall be well ventilated, dust & Vermin proof as per schematic diagram. The Panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Set | 3 |  |  | 0
a | INCOMER:
800A 4P MCCB (50kA) with Microprocessor Based Release for O/C, S/C (MICROLOGIC 2.0A) and ROM 1 no
AMMETER WITH SLECTOR SWITCH 1 no
12 Step Power Factor Relay 1 no
CT's 800/5A, 15VA, CL-1.0 for Metering 3 nos
Auto/ Manual Selector Switch 1 no
Off Delay Timer 1 no
Auxillary Contactors 1 set
Indicating Lamps - R, Y & B 1 set
2A, SP Control MCB, 10kA 1 set
100KVAR Capacitor Feeder comprising of: 1 no
200A TP MCCB (50kA) with TM Based Release for O/C, S/C and ROM. 1no
200A TP CONTACTOR 1 no
(100 x 1)kVAr MPP H- Duty, Capacitor Bank 100kVAr
Push Buttons - ON/OFF 1 sets
Indicating Lamps - ON/ OFF 1 sets
Auto/ Manual Selector Switch 1 no
2A, SP Control MCB, 10kA 1 set
50KVAR Capacitor Feeder comprising of: 2 no
125A TP MCCB (50kA) with TM Based Release for O/C, S/C and ROM 2 no
50 KVAR Capacitor Duty Contactor 2 no
(50 x 2)kVAr MPP H- Duty, Capacitor Bank 100kVAr
Push Buttons - ON/OFF 2 sets
Indicating Lamps - ON/ OFF 2 sets
Auto/ Manual Selector Switch 2 nos
2A, SP Control MCB, 10kA 2 nos
25KVAR Capacitor Feeder comprising of: 4 nos
63A TP MCCB (25kA) with TM Based Release for O/C, S/C and ROM. 4 nos
25 KVAR Capacitor Duty Contactor 4 nos
(25)kVAr MPP H- Duty, Capacitor Bank 100 kVAr
Push Buttons - ON/OFF 4 sets
Indicating Lamps - ON/ OFF 4sets
Auto/Manual Selector Switch 4 sets
2A, SP Control MCB, 10kA 4 sets
SECTION V - AMF PANEL
101 | Supply erection, testing and comiissioning of DG AMF Panel fully compatmentalized cubical type sheet steel clad floor mounted totally enclosed extensible on both sides switch board suitable for use on 430 V 3 phase 4 wire 50 c/s System having 50 KA fault capacity, housed with incoming and outgoing aluminium bus bars interconnection etc. with indication lmps, accessories etc. as required and complete with following incoming and outgoing switchgears with protection and metering etc. as per specification and schematic diagram complete as required. The panel shall be compatible with PLC/PCDG. The Panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 1 |  |  | 0
a | INCOMER: 2 NOS. 1250 & 1 No. 800 KVA DG SET (CABLE CONNECTION)
2000A TPN EDO ACB (50kA) with Microprocessor Based Release for O/C, S/C, E/F Protection & Shunt Trip Coil, U/V coil 2 nos
1600A TPN EDO ACB (50kA) with Microprocessor Based Release for O/C, S/C, E/F Protection & Shunt Trip Coil, U/V coil 1 no
Breaker Control Switch 3 nos
Digital Multifunction Meter, CL-1.0 (EM6400) With RS 485 Port 3 nos
Generator Protection Relay 3 nos
CT's 2000/5A, 15VA, CL-1.0 for Metering 6 nos
CT's 2000/5A, 15VA, CL-5P10 for Protection 6 nos
CT's 1600/5A, 15VA, CL-1.0 for Metering 3 nos
CT's 1600/5A, 15VA, CL-5P10 for Protection 3 nos
Auto/Manual Selector Switch 3 nos
Auxillary Contactors 3 sests
Indicating Lamps - R,Y,B & ON/OFF/Trip 3 sets
2A SP Control MCB, 10kA 3 sets
BUS COUPLER: (DUCT CONNECTION)
2000A FP EDO ACB (50kA) without release. 2 nos
Breaker Control Switch 2 nos
Auxillary Contactors 2 sets
ON Delay Timer 2 nos
Indicating Lamps - ON/OFF/Trip 2 sets
2A SP Control MCB, 10kA 2 sets
DG CONTROL AND RELAY PANEL FOR 3NOS. (DG) SETS
PUSH BUTTONS 3 sets
VOLTAGE RAISE/LOWER SELECTOR SWITCH 3 nos
SPEED RAISE/LOWER SELECTOR SWITCH 3 nos
EMERGENCY PUSH BUTTON 3 nos
EXCITATION AMMETER 3 nos
EXCITATION VOLT METER 3 nos
BATTERY CHARGER WITH DC VOLTMETER & AMMETER 3 nos
CHECK SYN RELAY 3 nos
AMF R3LAY 3 nos
MASTER TRIP RELAY 3 nos
TRIP CKT. SUPERVISION RELAY 3 nos
POWER PLC 1 no
DOUBLE VOLTMETER 1 no
DOUBLE FREQUENCY METER 1 no
MOTORISED POT. METER 3 nos
A/M SELECTOR SWITCH 3 nos
CRANKING RELAY 3 nos
TEMPERATURE SCANNER 3 nos
1KVA UPS 1 no
POWER SUPPLY UNIT, 230/ 24VDC 1 no
PT 415/RT3/110V/RT3 50VA CL 1.0 2 nos
16WINDOW ANNUNCIATOR 3 nos
MIMIC DIAGRAM 1 no
OUTGOINGS: CABLE CONNECTION
2000A 4P EDO ACB (50kA) with Microprocessor Based Release for O/C, S/C (MICROLOGIC 2.0A) 3 nos
Indicating Lamps 3 sets
Digital Multi Function Meter, CL-1.0 (EM6400) With RS 485 Port 9 nos
CT's 2000/5A, 15VA, CL-1.0 for Metering 6 nos
2A SP Control MCB, 10kA 3 sets
SECTION VI - Miscellaneous Item
102 | Supplying and fixing of non-skid rubber mat 12 mm thick and 900mm width as required including cutting to required lengths of approved make with Test Certificates for LT panels along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | SQM | 60 |  |  | 0
103 | Supplying, installing fixing of carbon diooxide fire extinguisher conforming to IS: 2878 with ISI mark along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. (4.5 Kg.) | Nos. | 7 |  |  | 0
104 | Supplying and fixing of first aid box as approved complete with standard kit as prescribed by Indian Red Cross along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 3 |  |  | 0
105 | Supply and fixing of HT Danger notice plate of 200 x 150mm made of mild steel at least 2mm thick and vitreous enamelled white on both side with inscription in signal red colour on front side as required as per IS: 2551 and along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Nos. | 9 |  |  | 0
SECTION VII - DG Set
106 | Supply, Installation, Testing and Commissioning of 1 Nos. 1250 KVA at 0.8 P.F (lagging), diesel engine alternator set mounted on common base frame complete with accessories as per specifications and layout, drawing with battery charger, battery and battery rack residential silencer, stainless steel bellows, 990 lts. day fuel tank, spring load GERB cush pads, electronic control panel, electronic governor etc. as required Radiator Cooled DG Sets along with acoustic enclosure as Per CPCB norms etc as required including exhaust pipe, fuel pipe, suitable cables connected to AMF panel and approval certificates from local authority and along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Sets | 1 |  |  | 0
SUB TOTAL OF PART C: ELECTRICAL WORKS | [5 empty] | 0

## P - D (HVAC)
BILL OF QUANTITY
PART D: HVAC WORKS
Sr. No. | Description of Items | Unit | Quantity | Rate In INR | Rate In Words | Amount In INR
Section-I: AIRCONDITIONING:
1 | Supply and fixing of aluminium powder coated fresh air louvers with bird screen and volume control damper in accordance with approved shop drawings and specifications. | Sqm | 1.6 |  |  | 0
2 | Supply, connecting and fixing extra length of copper piping (both pipes) with separate insulation for split type air conditioners etc complete as required | Rm | 1276 |  |  | 0
3 | Supplying installation testing and commissioning of GSS Ducting of following thickness including necessary supports etc , complete as per specifications.
(a) | 24 G | Sqm | 952 |  |  | 0
4 | Supply and fixing AcousticLining on ducts 18 mm Thickness, Density 8-11 Kg/m³ melamine foam. | Sqm | 191 |  |  | 0
5 | Supply and fixing Thermal Insulation on ducts 25 mm Thickness, Density 33±4 Kg/m³, XLPE Foam. | Sq.M | 952 |  |  | 0
6 | Supply and fixing of PVC Drain pipes 32 MM, with 6 mm nitril rubber insulation | Rm | 289 |  |  | 0
7 | Supply and fixing of Extruded Aluminium powder coated supply air Diffusers with aluminium control Dampers . | Sq.M | 27 |  |  | 0
8 | Supply and fixing of Extruded Aluminium powder coated Return air Diffusers. | Sq.M | 27 |  |  | 0
9 | Supply and fixing of Canvass Connection. Double layer,Fire resistant | Nos | 61 |  |  | 0
10 | Supply and fixing of Dryair Filters required at outdoor units on liquid line. | Nos | 61 |  |  | 0
11 | MS Stand for out door units. | Nos | 67 |  |  | 0
Section-II: EVAPORATIVE COOLING:
12 | Spray filled Air WasherSupply and installation Spray filled double skin, Floor Mounted, Horizontal Air Washer of 40,000 cfm rating against a SP of 70mm WG. Air Washer will be complete with following. 1) 25mm thick insulated panels, injected with 38 kg/m³ density PUF. 2) Outer skin made of 22G (0.6mm thick) pre coated steel sheet. 3) Inner skin made of GI sheet of 22G (0.6mm thick) 4) Imported DIDW backward curve centrifugal fan of 40,000 cfm/70 mm WG static pressure, outlet velocity -9.3 m/sec.
(a) | 40000 CFM | Set | 11 |  |  | 0
13 | Supply and Installation GI duct work, factory fabricated spotless GP sheets, GI flanges & cleats, gaskets, GI nuts and bolts and threaded rods. All ducts pieces shall be fully fabricated in factory and joined together at site. Duct fabrication and duct supports shall be as per IS-655.
a | 24 G | Sq.M | 595 |  |  | 0
b | 22 G | Sq.M | 1596 |  |  | 0
c | 20 G | Sq.M | 235 |  |  | 0
14 | Supply, installation, of DIDW centrifugal fan, belt drive forward curve, and factory supplied cabinet, consisting of motor, drive arrangement, base frame, cushy foot mounting and Accessories as per specification & drawing.
(a) | 16,000 CFM, 25MM SP,5.5 KW | Nos | 4 |  |  | 0
(b) | 8000 CFM, 25MM SP,2.2 KW | Nos | 32 |  |  | 0
15 | Supply and fixing of Powder coated Cont. Aluminium supply air Grill. Grills shall have flange on all four sides. | Sq.M | 152 |  |  | 0
16 | Supply and fixing of 40Ø GI B class drain piping from Air Washer drain point and Monobloc pump up to nearest drain sump complete with masonry pipe supports with Pcc uthalas.
(a) | 40 mm | Rm | 44 |  |  | 0
SECTION-III: AIR VENTILLATION:
17 | Supplying installation testing and commissioning of GI Ducting of following thickness including necessary supports adjustable dampers etc , complete as per specifications.
(a) | 24G | Sq.M | 112 |  |  | 0
(b) | 22G | Sq.M | 675 |  |  | 0
18 | Supply and fixing of Extruded Aluminium powder coated supply air Diffusers with aluminium control Dampers . | Sq.M | 8 |  |  | 0
19 | Supply and installation of Centrifugal DIDW, Exhaust air fans 4000CFM.
(a) | 4000 CFM | Nos | 4 |  |  | 0
SUB TOTAL OF PART D: HVAC WORKS | [5 empty] | 0