|  | NAYA RAIPUR DEVELOPMENT AUTHORITY |  |
| --- | --- | --- |

Tender document for Design, Supply, Installation, Testing and Commissioning of LED Street Lights and High Mast Lighting system along with power supply infrastructure development at Naya Raipur.

(Following Three-Envelope Tender Procedure)

Schedule – A

Price tender

To be submitted in ENVELOPE-3

NIT no. 9 /ST-LED/ELECT/CE(E)/NRDA/2012-13, Raipur,                                                            Dated: 07.02.2013

Issued by:   	Chief Executive Officer,

Naya Raipur Development Authority (NRDA)

Near Old Mantralaya Mahanadi Dwar

Raipur 492 001, Chhattisgarh

Tel: (0771) 4066011, Fax: (0771) 4066188,

E-mail: ceo@nayaraipur.com

Abstract of Design, Supply, Installation, Testing and Commissioning of LED Street Lights and High Mast Lighting system along with power supply infrastructure development at Naya Raipur.

| Sr. no. | Description of Items | Amount in INR |
| --- | --- | --- |
| A | Street Lighting |  |
| B | Cable work |  |
| C | High Mast |  |
| D | Transformer Installation |  |
| E | Installation of RMU, GPRS Enabled Remot Control Unit and Yard fencing |  |
|  | Total Amount in INR |  |

Cost of Estimates for Design, Supply, Installation, Testing and Commissioning of LED Street Lights and High Mast Lighting system along with power supply infrastructure development at Naya Raipur.

| S.No. | Item Description | Unit | Quantity | Rate in Rs. | Amount in Rs. |
| --- | --- | --- | --- | --- | --- |
| A | Street Lightning |  |  |  |  |
| 1 | Designing and providing suitable M-20 RCC foundation size 600x600x2000 mm for 10 meters of high GI octagonal pole including steel reinforcement (minimum 90kg per cum), form work, embeding 2 nos 50mm dia PVC pipe for cable entry in each foundation, excavation disposal of surplus soil and curing etc. as required.( 0.72 cum per pole) | cum | 246.96 |  |  |
| 2 | Supply of hot dipped galvanized (in single dip to average 70 micron) octoganal pole made of 4mm thick steel plate having base plate 240x240x16mm, window and flush cover with locking arrangement at suitable height from base for cable termination block, pole suitably reinforced with welded steel section at window cut section to make the strength of pole unaffected, including template and anchor plate 240x240x3mm with 4 nos 700mm long, 20mm dia foundation bolts (EN8 grade). |  |  |  |  |
| a | 10 metre high, minimum dia 151mm at bottom and 75mm at top | Each | 382 |  |  |
| 3 | Erection of GI octogonal pole on existing cement concrete foundation having grouted bolts and nuts, aligning in true vertical position as required. |  |  |  |  |
| a | 10 metre high | Each | 382 |  |  |
| 4 | Supply and fixing following street light pole bracket on existing pole made out of 50 mm dia MS "B" class pipe welded to 300 mm long MS pole canopy of suitable dia at a angle of 102.50 including having MS triangular stiffner of size 150 X 50 X 5 mm thick, making arrangement for tightening the bracket with pole by providing suitable size heavy duty nuts and bolts in canopy, painting with one coat of approved steel primer etc. as required. |  |  |  |  |
| a | Single Over Hang 1.50 metre Long - Decorative | Each | 324 |  |  |
| b | Double Over Hang 1.50 metre Long Decorative | Each | 58 |  |  |
| 5 | Supplying, installation, testing and commissioning of following 230/250 volts LED treet light fitting with gear box, igniter, with IP 65 protection on pole bracket complete but without lamp as required. |  |  |  |  |
| a | not more than 215 W | Each | 356 |  |  |
| b | not more than 160W | Each | 84 |  |  |
| 6 | Supplying, fixing, testing and commissioning of following 230/250 volts HPSV lamp tubular/elliptical in existing lighting luminaries on pole/ wall/ roof etc as required. |  |  |  |  |
| a | 250 watt(E) | Each | 0 |  |  |
| 6 | Design, Fabrication, Supply, Erection, Testing and commisioning of Powder coated, Weather Proof Double door type Feeder pillar fabricated out of 14 guage CRCA sheet steel in cubical, free standing, dust and vermin proof, with reinforcement of suitable size angle iron, channel, T -iron or flats as required. Feeder pillar shall be treated with all anti-corrosive process before painting as per specification. Feeder Pillar shall be suitable for 415V, 3-Phase, Four wire, 50 Hz supply complete with earth bus and lifting hooks as required in case of large panels.Approval shall be taken for each panel before fabrication. (All hardwares like nuts and bolts used shall be Galvanized and Zinc passivated) | Set | 11 |  |  |
|  | INCOMER |  |  |  |  |
|  | 1No. 4 Pole 100A TPN MCCB (35 KA) |  |  |  |  |
|  | 1No. 100A FP Contactor, AOM switch & Timers for 24 Hrs. setting |  |  |  |  |
|  | Metering & Indication |  |  |  |  |
|  | 1 set of phase indicating lamps |  |  |  |  |
|  | BUS-BAR |  |  |  |  |
|  | 1 Set of 100A TPN Aluminium Bus Bar with colour coded PVC Sleeves |  |  |  |  |
|  | OUTGOINGS |  |  |  |  |
|  | 6 Nos. 32A FP MCB |  |  |  |  |
|  | GPRS Based Remot Control Unit housed inabove proposed feeder pillar | Set | 11 |  |  |
|  | Earthing with G.I. earth pipe 3.0 mtr long, 40 mm dia including accessories with charcoal Sand or bentonide powder as required. | Set | 382 |  |  |
|  | Sub total (A) |  |  |  |  |

| S.No. | Item Description | Unit | Quantity | Rate in Rs. | Amount in Rs. |
| --- | --- | --- | --- | --- | --- |
| B | Cable work |  |  |  |  |
| 1 | Supplying and laying double wall HDPE pipe having corrugation on the outer wall and plan surface on inner wall in ground below road, path etc at a depth not less than 40 cm including excavation, dismantling of road if required and refilling the trench etc. as required. |  |  |  |  |
| a | 40 mm | mtr | 14400 |  |  |
|  | 90 mm | mtr | 3000 |  |  |
| 2 | Supplying and laying following sizes one number PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade in existing RCC/ HUME/ STONEWARE/ METAL pipe as required. |  |  |  |  |
| a | 3.5 x 16 sq. mm. (pole to pole) |  | 17175 |  |  |
| b | 3.5 x 50 sq. mm. (pole to pole) |  | 2550 |  |  |
| c | 3.5 x 70 sq. mm. (transformer to feeder pillar) | mtr | 450 |  |  |
| 3 | Supplying and making end termination with brass compression gland and aluminum lugs for following size armoured aluminum conductor power cable of 1.1 KV grade as required. |  |  |  |  |
| a | 3.5 x 16 sq. mm. | Each | 64 |  |  |
| b | 3.5 x 50 sq. mm. | Each | 48 |  |  |
| c | 3.5 x 70 sq. mm. (transformer to feeder pillar) | Each | 16 |  |  |
| 4 | Supplying, fixing and cramping suitable size and all type aluminium ferule/ lugs to following size 1.1 KV grade power cable core/ lead, pressed with high pressure cramping tool including connection to switch gear/ MCCB etc as required. |  |  |  |  |
| a | 3.5 x 16 sq. mm. | Each | 3056 |  |  |
| b | 3.5 x 35 sq. mm. | Each | 20 |  |  |
| c | 3.5 x 50 sq. mm. | Each | 100 |  |  |
| d | 3.5 x 70 sq. mm. (transformer to feeder pillar) | Each | 120 |  |  |
| 5 | Supplying and making straight through joint with heat shrinkable joint kit including aluminium ferrules for following size of PVC insulated and PVC sheathed / XLPE aluminum conductor cable of 1.1 KV grade as required. |  |  |  |  |
| a | 3.5 x 50 sq. mm. (pole to pole) | Each | 2 |  |  |
| b | 3.5 x 70 sq. mm. (transformer to feeder pillar) | Each | 6 |  |  |
| 6 | Supply and drawing following sizes of FR PVC insulated copper conductor, single core cable in the existing surface/ concealed, steel/ PVC conduit as required. |  |  |  |  |
| a | 3x1.5 sq.mm. (from Pole Junction box to Light fitting) | mtr | 4840 |  |  |
|  | Sub total |  |  |  | 0.00 |
| C | HIGH MAST |  |  |  |  |
| S.No. | Item Description | Unit | Quantity | Rate in Rs. | Amount in Rs. |
| 1 | Supply, erection, testing & commissioning of High Mast Lighting system (as per CP3-TRT/1996 of ILE,UK) consisting of totally hot dip galvanised by single dip method high mast, lantern, carriage suitable for upto 12 nos. Luminiares, mast-head assembly, 2 nos. Aviation obstruction Neon lights, double drum type self sustaining winch, integral power tool (winch motor with control circuit), hot dip galvanised heavy duty pipe Lightning Finial, suitable ropes and Cement concrete foundation of M-20 grade complete as required. The mast is constructed from M.S. plate (as per BS-EN 10025) cut & folded to form a polygonal section, telescopic jointed and welding as per BS-5135. The complete work shall be supervised and certified by the manufactures for satisfactory supply, erection, testing & commissioning of high mast. |  |  |  |  |
| a | 20 Mtr HM (in 2 section) | Each | 2 |  |  |
| 2 | Supplying, installation, testing and commissioning of following 230/250 volts metal halide wide beam Flood light luminaires with weather-proof gear box, igniter, capacitor with IP 66 protection on Wall surface/ building parapet/ pole bracket complete but without lamp as required. (for High mast only) |  |  |  |  |
| a | 1 x 400 Watt (t) | Each | 24 |  |  |
| 3 | Supplying, fixing, testing and commissioning of following 230/250 volts metal halide lamp in existing lighting luminaries fixed on pole/ wall/ roof etc as required. |  |  |  |  |
| a | 400 Watt (BT) | Each | 24 |  |  |
|  | Sub Total( C ) |  |  |  |  |
| D | Transformer Installation |  |  |  |  |
| S. No. | Item Description | Unit | Quantity | Rate in Rs. | Amount in Rs. |
| 1 | 2 | 3 | 4 | 5 | 6(4x5) |
| 1 | Supply, Installation, Testing & Commissioning of floor mounted RMU comprising of 1 nos. 12 kV, 630 A LBS complete with accessories, hard wares etc. as required for completeness as per attached specification/ drawing, CSPDCL standards and direction of EIC. One of the LBS shall controlled distribution transformer and particular LBS shall have neon indication lamp and the 30 A HRC fuses. | No. | 6 |  |  |
| 2(i) | Supply Installation, testing & commissioning of 11/ 0.433 KV, 63 KVA BEE 3 Star rating distribution transformer with out tap changer, Al wound, oil cooled suitable for outdoor use with required fittings, accessories,both side cable terminal box, hardwares etc. as required for completeness as per attached specification/drawing, CSPDCL standards and direction of EIC. | Nos | 5 |  |  |
| 2(ii) | Supply Installation, testing & commissioning of 11/ 0.433 KV, BEE 3 star 25 KVA distribution transformer with out tap changer, Al wound, oil cooled suitable for outdoor use with required fittings, accessories,both side cable terminal box, hardwares etc. as required for completeness as per attached specification/drawing, CSPDCL standards and direction of EIC. | No | 1 |  |  |
| 3 | Design, Fabrication, Supply, Erection, Testing and commisioning of Powder coated, Weather Proof outdoor type Double door type LT DB fabricated out of 14 guage CRCA sheet steel in cubical, free standing, dust and vermin proof, with reinforcement of suitable size angle iron, channel, T -iron or flats as required. LT DB shall be treated with all anti-corrosive process before painting as per specification. Feeder Pillar shall be suitable for 415V, 3-Phase, Four wire, 50 Hz supply complete with earth bus and lifting hooks as required in case of large panels.Approval shall be taken for each panel before fabrication. (All hardwares like nuts and bolts used shall be Galvanized and Zinc passivated) | Set | 6 |  |  |
|  | INCOMER |  |  |  |  |
|  | 1No. 4 Pole 100A TPN MCCB (35 KA) |  |  |  |  |
|  | Metering & Indication |  |  |  |  |
|  | 1 set of phase indicating lamps |  |  |  |  |
|  | BUS-BAR |  |  |  |  |
|  | 1 Set of 100A TPN Aluminium Bus Bar with colour coded PVC Sleeves |  |  |  |  |
|  | OUTGOINGS |  |  |  |  |
| 4 | 3 Nos. 40 A FP MCB |  |  |  |  |
|  | Supplying and laying following sizes one number XLPE, steel armoured, aluminium conductor power cable of 11 KV grade in existing masonry open duct as required. |  |  |  |  |
| 5 | Single Runs 3 core 50 sqmm | Mtrs | 60 |  |  |
| 6 | Supply, installation, testing & commissioning of cable termination kits of push on/ heat shrinkable type for indoor/ outdoor terminations of 11 KV, XLPE AL Cable of 3C X 50 sqmm complete with double compression gland, lugs, tags, accessories, hardwares etc. as required for completeness as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Nos. | 12 |  |  |
| 8 | Supply of all materials, installation, testing and commissioning of GI pipe electrode as per IS: 3043 comprising of 40mm dia, 2.9mm thick, 3m long class A GI pipe with flange, 16nos. 12mm dia through holes buried in a pit. The scope shall cover excavation in all kinds of soil and rock, filling the pit with equal proportion of salt and charcoal in layers of 300mm depth, 150mm wide alround the pipe from bottom upto a depth of 300mm below the masonary chamber, refilling by excavated soil free from rock and shark edges; provision of watering arrangement with GI funnel and wire mesh be enclosed in a brick masonary chamber of 400mm x 400mm x 400mm with removable RCC cover on top. The connection from the flanges of the pipe shall be established by 50mm x 6mm GI strip using 12mm dia GI hardwares. The work shall be carried out with accessories, hardware etc as required for completeness and as per attached specification/drawing, CSPDCL standards and direction of EIC. | Nos. | 30 |  |  |
| 9 | Supply, running and terminating of GI materials as earth continuity conductor to earth all the metallic parts/ neutral of transformer/ lightning arrestors, control room equipments to earth electrodes with accessories, hardwares etc. as required for completeness, as per attached specification/ drawings, CSPDCL standards and direction of EIC. |  |  |  |  |
|  | i) 50mm x 6mm strips | mtrs | 60 |  |  |
|  | ii) G.I wire of size 8 SWG to 6 SWG | Mtrs | 90 |  |  |
| 10 | Construction of plinth for transformer, RMU and LTDB in RCC construction for installation of transformer, associated RMU, LTDB including excavation, laying of PCC, neatly dressed, plastered, supply of all materials as required for completeness, as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Cm | 20 |  |  |
| 11 | Yard fencing (5x3 meter) with chain link mesh conform ISI 2721/1989 size (75 x75)mm & 8mm gauge of chain link wire with 4 mm thick GI Wire on top & bottom of mash, on main bracket of Angel (65 x65 x 5 mm) & bracing with Angel (50x50x6mm) of 2.5 m long 3.m with bracket gate & murrom, gravel filling all on A class civil work Construction with accessories, hardwares etc. as required for completeness, as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Rmt | 96 |  |  |
| 12 | Construction of RCC cable trench with removable RCC covers of size 900 (w) x 600(D) mm, including supply of all required materials as required for completeness, as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Rmt | 60 |  |  |
|  | Sub total Amount (D) |  |  |  |  |
| E | Installation of RMU with Yard fancing on Road no 4, 9A, 12, 10 and Installation of GPRS based Remot Control System on Exisiting Feeder pillars |  |  |  |  |
| S. No. | Item Description | Unit | Quantity | Rate in Rs. | Amount in Rs. |
| 1 | 2 | 3 | 4 | 5 | 6(4x5) |
| 1 | Supply, Installation, Testing & Commissioning of floor mounted RMU comprising of 1 nos. 12 kV, 630 A LBS complete with accessories, hard wares etc. as required for completeness as per attached specification/ drawing, CSPDCL standards and direction of EIC. One of the LBS shall controlled distribution transformer and particular LBS shall have neon indication lamp and the 30 A HRC fuses. | No. | 22 |  |  |
|  | Supplying and laying following sizes one number XLPE, steel armoured, aluminium conductor power cable of 11 KV grade in existing masonry open duct as required. |  |  |  |  |
| 5 | Single Runs 3 core 50 sqmm | Mtrs | 250 |  |  |
| 6 | Supply, installation, testing & commissioning of cable termination kits of push on/ heat shrinkable type for indoor/ outdoor terminations of 11 KV, XLPE AL Cable of 3C X 70 sqmm complete with double compression gland, lugs, tags, accessories, hardwares etc. as required for completeness as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Nos. | 44 |  |  |
| 8 | Supply of all materials, installation, testing and commissioning of GI pipe electrode as per IS: 3043 comprising of 40mm dia, 2.9mm thick, 3m long class A GI pipe with flange, 16nos. 12mm dia through holes buried in a pit. The scope shall cover excavation in all kinds of soil and rock, filling the pit with equal proportion of salt and charcoal in layers of 300mm depth, 150mm wide alround the pipe from bottom upto a depth of 300mm below the masonary chamber, refilling by excavated soil free from rock and shark edges; provision of watering arrangement with GI funnel and wire mesh be enclosed in a brick masonary chamber of 400mm x 400mm x 400mm with removable RCC cover on top. The connection from the flanges of the pipe shall be established by 50mm x 6mm GI strip using 12mm dia GI hardwares. The work shall be carried out with accessories, hardware etc as required for completeness and as per attached specification/drawing, CSPDCL standards and direction of EIC. | Nos. | 110 |  |  |
| 9 | Supply, running and terminating of GI materials as earth continuity conductor to earth all the metallic parts/ neutral of transformer/ lightning arrestors, control room equipments to earth electrodes with accessories, hardwares etc. as required for completeness, as per attached specification/ drawings, CSPDCL standards and direction of EIC. |  |  |  |  |
|  | i) 50mm x 6mm strips | mtrs | 220 |  |  |
|  | ii) G.I wire of size 8 SWG to 6 SWG | Mtrs | 440 |  |  |
| 10 | Construction of plinth for transformer, RMU and LTDB in RCC construction for installation of transformer, associated RMU, LTDB including excavation, laying of PCC, neatly dressed, plastered, supply of all materials as required for completeness, as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Cm | 55 |  |  |
| 11 | Yard fencing (5x3 meter) with chain link mesh conform ISI 2721/1989 size (75 x75)mm & 8mm gauge of chain link wire with 4 mm thick GI Wire on top & bottom of mash, on main bracket of Angel (65 x65 x 5 mm) & bracing with Angel (50x50x6mm) of 2.5 m long 3.m with bracket gate & murrom, gravel filling all on A class civil work Construction with accessories, hardwares etc. as required for completeness, as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Rmt | 352 |  |  |
| 12 | Construction of RCC cable trench with removable RCC covers of size 900 (w) x 600(D) mm, including supply of all required materials as required for completeness, as per attached specification/ drawing, CSPDCL standards and direction of EIC. | Rmt | 220 |  |  |
|  | GPRS Based Remot Control Unit housed in eisting feeder pillar | Set | 59 |  |  |
| 13 | Sub total Amount (1 to 12) |  |  |  |  |

Signature of Tenderer

with Seal