SCHEDULE– D Section-II

Scope of work

# Works Requirement

This section contains the brief idea of scope of work, supplementary information drawings etc. regarding the work to be executed under instant tender, may vary as per site requirement. In case of any change the decision of Engineer-in-charge will be final and binding to the contractor.

Section-A : Site Information

- SITE INFORMATION

1.1 Work Site

    - The project site is on Road no 2, 3, 6, 7 and stadium Interconnection Road located in the Naya Raipur.

    - The Contractor shall plan his works keeping in view restriction of approach and availability of space and time.

  - GENERAL CLIMATIC CONDITIONS

    - The area in which the work lies is mostly plain terrain.

    - The highest and lowest temperatures in general range from 48 degree Celsius to 8 degree Celsius.

    - Summer season is from April to June and winter season is from November to March.

    - The mean average annual rainfall in the area over a five-year period is of the order of 1065 mm, a good portion of which is concentrated during July to mid September, when about 75% of the annual rainfall occurs.

    - Naya Raipur experiences extreme climatic conditions and Bidders must acquaint themselves about the same before submitting the Bid. The Employer shall in no way be responsible on this account.

The above site information is being made available to Bidders in good faith and Bidders are advised to obtain relevant information, as may be considered necessary by them, before quoting for the bid. No claims whatsoever on account of any discrepancy in the above information shall be admissible to Bidders.

Section-B : Scope of Work

- Objective:-

The objective of the contract is to design, supply, erection, installation, testing and commissioning of LED street lights and High Mast on above mentioned Roads and Junctions of Naya Raipur as per stipulated standards and within the time stipulated by the Contract along with power supply infrastructure development. In full recognition of this objective, and with full acceptance of the obligations, liabilities and risks which may be involved, the Contractor shall undertake the execution of the Works.

- SCOPE OF WORKS

The work under this contract shall be carried out in accordance with the various documents constituting the contract and shall consist of various salient items for design, supply, erection, installation, testing and commissioning of LED street lights and High Mast along with development of  Infrastrucutre with a total length of approx. 7.2 kms and 2 nos. High Mast.

The broad scope for the proposed work shall be

- Supply, installation, testing and commissioning of LED streetlight systems with all fixtures, fittings and related works. Details of the work site are given below:

| Sr No. | Particulars | Road No. 3, 6 and 7 | Road No 7 | Road No. Stadium Interconnection Road |
| --- | --- | --- | --- | --- |
| 1 | Length of road | Appox 5.5 km | Approx 0.5 Km | Approx 1.5 Km |
| 2 | Carriageway | Dual carriageway | Dual carriageway | Dual carriageway |
| 3 | Road Width | 100 mtr | 60 mtr | 40 mtr |
| 4 | Average Carriageway width | 7.5 mtr | 7.5 mtr | 7.5 mtr |
| 5 | Median | 5 mtr | 5 mtr | 1.2 mtr |
| 5 | Pole to pole distance | 35 mtr | 35 mtr | 28/30 mtr |
| 5 | Mounting Height | 10 mtr | 10 mtr | 10 mtr |
| 8 | Layout of poles | On Road side both end | On Median | On Median |
| 9 | street light pole bracket | Single Over Hang | Double Over Hang | Double Over Hang |

Location for High Mast

- Interconnection junction of  Road No. 2, Road No. 5 and Road no. 11 near Uparwara village.

- Interconnection junction of  Road No. 2 and  Road No. 6

- Construction of plinth for transformer, Oil type  RMU & Distribution Box.

- Installation of 25/63 KVA 3 Star Distribution Transformers, oil type RMU & Distribution Box.

- Fencing with fabrication of gate for distribution transformer substation.

- Installation of   GSM base LED Street Light automation system with supply of software.

- Construction of plinth for Oil type RMU & Distribution Box in existing Distribution transformers.

- Fencing with fabrication of gate for existing distribution transformer substations.

- Design of LED Street Light for proposed Road at Naya Raipur shall be carried out on following Illumination parameters:

  - Average illumination level for main carriageway must be 30 lux Average and at junction point average illumination level must be 50 lux.

  - Average illumination level for service road & reserve area should be within 50-75% of illumination level (lux) of main carriageway.

  - Maintenance factor to be considered as 0.90

  - Uniformity factor = minimum illumination level/ average illumination level should be: 0.4

  - Traverse Uniformity factor = minimum illumination level/ maximum illumination level should be: 0.33.

  - Design should be such that glare is minimum so that driver feel comfort while driving.

  - Design submitted by the bidder must clearly show the median, main carriageway, shoulder. Design must make through dialux software. All file of the generated output must be submitted in soft copy as well as hard copy. IES file of the specified light product must be submitted in soft copy for verification purpose. Any error or overwriting shall not be acceptable. (Mandatory)

  - The design criteria shall be fulfilled. The light product, driver current, lumen output, input wattage and other relevant details in design shall be considered for technical evaluation of the rest criteria. If any deviation found in parameter of driver current, lumen output, input wattage of specified light product in the type test reports from design data; the test report will not be accepted.

    - Within 15 days of award of work the approved tenderer shall submit detailed drawings showing the LED Street Light pole location, High Mast location, Pole/High Mast foundation details, cable movement, feeder pillar position etc.

- Supply, installation, testing and commissioning of various items as described in the BoQ for LED Street Light & High Mast and as per approved drawing including all accessories, feeder pilar and heat resistant flexible cables for final connections and terminations.

- The period of defect liability shall be 24 months after successful commissioning.

- The Contractor will be required to rectify any deficiencies which are attributable to defects in the workmanship or quality of materials, Plant or equipment during the Contract Period and defect liability period.

- The records maintained by the contractors shall be produced periodically to the Engineer-in-charge for proper monitoring as desired by NRDA.

b)	The tenderer should provide the facility in conformity with the relevant codes, rules and regulations.

- The tenderer should ensure that they provides all the documentation including general arrangement drawing wiring diagrams and instructions for installation and operation of the lighting fixtures.

- The Tender will have to provide their engineer’s in pre commissioning checks and tests and commissioning of the lighting fixtures.

- As Build Drawings

- The Contractor will supply four hard copies & softcopy of   the   as built   drawings of completed work.

- The cost of preparing all such items of work shall be deemed to have been included in the respective rates/ prices quoted by the Contractor in the “Bill of Quantities.”

- The price quoted shall include all the activities as mentioned in the scope of work, in addition to contingencies required for the above scope of work.

- ENVIRONMENTAL CONSIDERATIONS

All provisions and conditions contained in the Bid documents and other statutory provisions regarding environmental protection, safety & health shall be strictly complied with and shall be incidental to work.

- STANDARDS

(1) 	Equipment, materials and systems shall be designed, manufactured and tested in accordance with the latest issue of International and/or National codes and standards. The Contractor shall submit copies to the NRDA of all codes and standards used for the work.

(2) 	Reference to standards or to materials and equipment of a particular manufacturer shall be regarded as followed by the words “or equivalent”. The Contractor may propose alternative standard materials, or equipment that shall be equal to or better than those specified. If the Contractor for any reason proposes alternatives to or deviations from the specified standards, or desires to use materials or equipment not covered by the specified standards, the Contractor shall apply for the consent of the NRDA. The Contractor shall state the exact nature of the change, the reason for making the change and relevant specifications of the materials and equipment in the English language. The decision of the NRDA in the matter of quality will be final.