SCHEDULE– D

Section-III

Technical Specification of Works

The broad design specifications for the works are provided in this section of document, but the general specifications for all works are provided in Notice Inviting tender

INDEX

| Sr. No. | Description |
| --- | --- |
| 1 | Specifications of Octagonal Poles |
| 2 | Highmast – Technical Specification |
| 3 | Technical Specification for Earthing System |
| 4 | LT XLPE Power Cables |
| 5 | Cable Laying |
| 6 | HDPE Pipes |
| 7 | Street Light Feeder Pillar (SLFP) |
| 8 | Cables tags and markers |
| 9 | Cable Lugs |
| 10 | Cable Termination and Connection |
| 11 | MCCB |
| 12 | Light Fixture and Lamps |
| 13 | Distribution Transformers |
| 14. | Street Light Automation System |
| 15. | 11 kV Oil Type RMU |

- SPECIFICATIONS OF OCTAGONAL POLES

This specification determines the requirements of the octagonal poles in respect of design, manufacture, testing and supply of Galvanised Poles, Base Plate and Bracket Arms for use in Street Lighting.

  - SCOPE :

This specification covers tapered octagonal single piece columns of required mounting height. Octagonal poles shall be of flanged type to be fixed on the foundation bolts. Possible loading configurations for different types of octagonal poles are indicated in respective GA drawings.  The octagonal poles shall be designed for 180 Km/Hr. Maximum wind speed

  - GENERAL STANDARDS :

- Design:

The polygonal pole structure shall be designed to sustain basic wind speed of 50 m/sec, with 3 sec gust and measured at a height of 10 meters. The safety factor for wind load in ultimate limit state shall be taken as 1.5. The structure shall conform to IS 875-Part3:1987 relating to wind load on structures and also conform to BSEN 40-1:1992 relating to general construction. The top loading i.e. area and the weight of fixtures are to be considered to calculate maximum deflection of the pole and the same shall meet the requirement of BSEN 40-3:2000, pr EN-40-3-3.

The grade of steel used shall be S-355 as per BSEN-10025 or equivalent Indian Standards. Manufacturing of poles shall be done out of Manufacturer supplies straight sheet to eliminate deformity due to decoiling of rolls.

For the Design of Octagonal Poles, the Structural Calculation Details, confirming the suitability as per standards,   shall be produced by the successful tenderer.

- Pole Shaft:

The pole shaft shall have octagonalcross section and shall be continuously tapered with single longitudinal welding. There shall not be any circumferential welding. The welding of pole shaft shall be done by submerged arc welding process. The Octagonal pole shafts shall be provided with the rigid flange plate of suitable thickness with provision for fixing four foundation bolts. The base plate shall be fixed by welding to the pole shaft at two locations i.e. from inside and outside. Bending of the sheet into polygonal shape shall be done through a CNC controlled, Laser aligned single blade bending process. Foundation accessories will be as per IS 1367.

- Door Opening:

Polygonal poles shall have door of approximate 500 mm length at the elevation of 1500 mm from the base plate. The door shall be vandal resistance and shall be weather proof to ensure safety of inside connections. The door shall be flush with the exterior surface and shall have suitable locking facility. The door cutting shall be with smooth finish performed with CNC cutting machine. The pole shall be adequately strengthened at the location of the door to compensate for the loss in section. The pole shall be additionally reinforced with a welded steel section, so that the section at door is unaffected and undue bucking of the cut section is prevented.

- Material

Octagonal Poles HT Steel Conforming to grade S355JO.   Base Plate Fe 410 conforming to IS 226 / IS 2062.  Test Certificates from the Steel Manufacturer for the above to be produced by the successful tenderer.

- Pole  sections

The Octagonal Poles up to the length of 10 meters shall be in single piece with single longitudinal welding joint.    There shall not be any circumferential weld joint.

- Galvanization:

All components of the columns and brackets shall be hot dip galvanized after completion of fabrication. No further touching up, finishing or modification shall be done after galvanizing. The overall length of each section/bracket shall be immersed in one dipping operation.

The galvanizing coating shall be smooth, continuous and uniform. It shall be free from acid spots and shall not scale or blister nor be removable while handing or packing.

There shall be no impurities in the zinc nor additives to the smaller bath which could have a deleterious effect on the zinc coating.

Before pickling, all welding, drilling, cutting, binding etc. must be completed and all grease, paint, varnish, oil, welding slag etc. completely removed. All protuberances, which should affect the life of the galvanizing should also be removed.

During pickling each article shall be completely immersed in one dip.  Care shall be taken to WEIGHT OF ZINC COATING.

The poles shall be single dip, hot galvanized as per IS: 2629/IS 2633/IS 4759 standards with minimum coating thickness of 85  microns.

- Base Flange:

The base plate shall be fabricated from steel plate free from laminations and mounted on RCC Foundation laid as per the approved drawing

- BRACKETS :

The bracket shall be hot dip galvanized after fabrication. The bracket shall be manufactured as per the3 GA drawing and with best workmanship.   The bending of the pipes shall be without any kinks/visible marks.  Arms shall be symmetrical.

- ELECTRICALS

The octagonal pole shall be provided with a door flush with the pole surface without any projection.   Required door reinforcement shall be determined by the manufacturer.   Inside the door a suitable plate shall be welded for mounting 6A, MCB and neutral link.  Three core 2.5 sq.mm copper wires shall be run for each luminaire individually.

- FACILITIES FOR TESTING

The manufacturer shall offer the purchaser or his authorized representative all the testing facilities required either at the works or in the vicinity thereof.

- DRAWING AND TECHNICAL DATA :

At the time of tendering the manufacturer must submit a detailed drawing for each column type offered.

- Overall length

- Base diameter across flats.

- Top diameter across flats.

- Wall thickness of column erections

- Flange base dimensions to include side length, thickness, slot sizes and anchor bolt fixing centres

- Door dimensions, corners radius and height above ground level

- Dimensions of cable entry slot (and for rooted columns the depths below the ground level).

- Dimensions and section of door reinforcement

- Dimensions of anchor bolts, nuts and washers

- Weight (KG) of each galvanized pole including flange base but excluding anchor bolts.

- FOUNDATION :

The design of foundation for pole shall be submitted along with the bid and detailed drawing of foundation indicating the size of template, foundation bolts etc. shall be enclosed.

- HIGHMAST – TECHNICAL SPECIFICATION:

- Structure:

The High Mast shall be of continuously tapered, polygonal cross section, at least 20 sided, presenting a good and pleasing appearance and shall be based on proven In-Tension design conforming to the standards referred to above, to give an assured performance, and reliable service. The structure shall be suitable for wind loading as per IS 875 Part - III 1987.  The mast dimensions shall be as per enclosed datasheet.

- Construction:

The mast shall be fabricated from special steel plates, conforming to BS-EN10025, S355 grade cut and folded to form a polygonal section as stated at 2.01 above and shall be telescopically jointed and welded.  The welding shall be in accordance with BS.5135/AWS.  The procedural weld geometry and the workmanship shall be exhaustively tested on the completed welds.  The mast shall be delivered in sections of effective length at site. Thus mast shall be supplied sections & each section shall be fabricated out of individual plates duly folded and welded. There shall be only one longitudinal seam weld per section. Sections fabricated out of multiple plates or with more than one weld shall not be accepted. At site the sections shall be joined together by slip-stressed-fit method. No site welding or bolted joint shall be done on the mast.

The minimum over lap distance shall be 1.5 times the diameter at penetration. The dimensions of the mast shall be decided based on proper design and design calculations shall be submitted for verification. The mast shall be provided with fully penetrated flange, which shall be free from any lamination or incursion. The welded connection of the base flange shall be fully developed to the strength of  the entire section.  The base flange shall be provided with supplementary gussets between the bolt-holes to ensure elimination of helical stress concentration.  For the environmental protection of the mast, the entire fabricated mast shall be hot dip galvanised, internally and externally, having a uniform thickness As per BSEN ISO-1461. The galvanizing has to be done by single dipping method only for better adhesion and life.

- Foundation

The foundation of the complete High Mast Unit shall be RCC foundation suitable for the soil where the High Mast Unit is proposed to be installed complete with the required foundation bolts. The soil, at that proposed location should be tested by the bidding company, at its own cost and the design of the proposed foundation with its foundation bolts should be prepared and certified by a registered structural engineer / consultant having atleast 15 years experience and should be got approved from the Civil Department of desired local engineer college before the execution of the foundation. The curing of the foundation must be done very thoroughly as per standard practice. The cured foundation should be got certified by a licensed structural engineer / consultant having at least 15 years experience. These certificates should be given in original to the Engineer - in charge.

- Capping

The capping section of the top pulley assembly unit should be of hot dipped galvanized MS material and shall contain the pulleys for stainless steel wire ropes and power cable and it must be ensured that the electrical cables and stainless steel wire ropes are completely separated before passing over their respective pulleys. The pulley-asembly should be protected by a suitable weather - proof cover.

- Door Opening:

An adequate door opening shall be provided at the base of the mast and the opening shall be such that it permits clear access to equipment like winches, cables, plug and socket, etc. and also facilitate easy removal of the winch.  The door opening shall be complete with a close fitting, vandal resistant, weatherproof door, provided with a heavy-duty double internal lock with special paddle key. The door opening shall be carefully designed and reinforced with welded steel section, so that the mast section at the base shall be unaffected and undue buckling of the cut portion is prevented. Size of door opening shall not be more than 1200 x 250 mm to avoid buckling of the mast section under heavy wind conditions.

- Dynamic Loading for the Mast:

The mast structure shall be suitable to sustain an assumed maximum reaction arising from a wind speed as per IS 875 (three second gust), and shall be measured at a height of 10 metres above ground level.  The design life of the mast shall be a minimum of 35 years.

a. 	Lantern Carriage:

2.06.1   Fabrication:

A fabricated Lantern Carriage shall be provided for fixing and holding the flood light fittings and control gearboxes.  The Lantern Carriage shall be of special design and shall be of steel tube construction, the tubes acting as conduits for wires, with holes fully protected by grommets.  The Lantern Carriage shall be so designed and fabricated to hold the required number of flood light fittings and the control gear boxes, and also have a perfect self balance. The Lantern Carriage shall be fabricated in two halves and joined by bolted flanges with stainless steel bolts and nyloc type stainless steel nuts to enable easy installation or removal from the erected mast. The inner lining of the carriage shall be provided with protective PVC arrangement, so that no damage is caused to the surface of the mast during the raising and lowering operation of the carriage. The entire Lantern Carriage shall be hot dip galvanized after fabrication.

2.06.2 Junction Box.

Weather proof junction box, made of Cast Aluminium shall be provided on the Carriage Assembly as required, from which the inter-connections to the designed number of the flood light luminaries and associated control gears fixed on the carriage shall be made.

- Raising and lowering mechanism:

For the installation and maintenance of the luminaries and lamps, it shall be necessary to lower and raise the Lantern Carriage Assembly.  To enable this, a suitable Winch Arrangement shall be provided, with the winch fixed at the base of the mast and the specially designed head frame assembly at the top.

2.07.1 Winch:

The winch shall be of completely self sustaining type, without the need for brake shoe, springs or clutches.  Each driving spindle of the winch shall be positively locked when not in use, by gravity activated PAWLS. Individual drum also should be operated for fine adjustment of lantern carriage.  The capacity, operating speed, safe  working load, recommended lubrication and serial number of the winch shall be clearly marked on each winch. The gear ratio of the winch shall be 53: 1.  However, the minimum-working load shall be not less than 750 kg. The winch shall be self-lubricating type by means of an oil bath and the oil shall be readily available grades of reputed producers.

The winch drums shall be grooved to ensure perfect seat for stable and tidy rope lay, with no chances of rope slippage. The rope termination in the winch shall be such that distortion or twisting is eliminated and at least 5 to 6 turns of rope remains on the drum even when the lantern carriage is fully lowered and rested on the rest pads. It should be possible to operate the winch manually by a suitable handle and by an integral power tool. Operation of the winch with manual handle shall be independent of the power tool. Winches with manual operation through the power tool shaft shall not be accepted. Individual drum operation of the winch shall be possible. A double drum winch shall have 2 drums and two worm gears independent in operation for increased safety. It shall be possible to remove the double drum after dismantling, through the door opening provided at the base of the mast. Also, a winch gearbox for simultaneous and reversible operation of the double drum winch shall be provided as part of the contract. The winch shall be type tested in presence of a reputed Institution and the test certificates shall be furnished before supply of materials. A test certificate shall be furnished by the Contractor for each winch in support of the maximum load operated by the winch.

2.07.2  Head Frame:

The head frame, which is to be designed as a capping unit of the mast, shall be of welded steel construction, galvanized both internally and externally after assembly. The  top pulley shall be of appropriate diameter, large  enough to accommodate the stainless steel wire ropes and the multi-core electric cable.  The pulley block shall be made of non corrodible material, and shall be of die cast Aluminium Alloy (LM-6). Pulley made of synthetic materials such as Plastic or PVC is not acceptable. Self-lubricating bearings and stainless steel shaft shall be provided to facilitate smooth and maintenance free operation for a long period. The pulley assembly shall be fully protected by a canopy galvanized internally and externally. Close fitting guides and sleeves shall be provided  to ensure that the ropes and cables do not dislodged from their respective positions in the grooves.  The head frame shall be provided with guides and stops with PVC  buffer for docking the lantern carriage.

2.07.3   Stainless Steel Wire Ropes:

The suspension system shall essentially be without  any intermediate joint and shall consist of only non-corrodible stainless steel of AISI 316. The stainless steel wire ropes shall be of 7/19 constructions, the central core being of the same material.  The overall diameter of the rope shall not be less than 6 mm.  The breaking load of each rope shall not be less than 2400kg. giving a factor of safety of over 5 for the system at full load  as per the TR-7 referred to in the beginning of this specification . The end constructions of ropes to the winch drum shall be fitted with talurit. The thimbles shall be secured on ropes by compression splices. Two continuous lengths of stainless steel wire ropes shall be used in the system and no intermediate joints are acceptable in view of the required safety. No intermediate joints/terminations, either bolted or else, shall be provided on the wire ropes between winch and lantern carriage.

- Electrical System, Cable and Cable Connections:

A suitable terminal box shall be provided as part of the contract at the base compartment of the high  mast for terminating the incoming cable. The electrical connections from the bottom to the top shall be made by special trailing cable. The cable shall be EPR insulated and PCP sheathed to get flexibility and endurance. Size of the cable shall be minimum 5 core 2.5 / 4.0 sq mm copper. The cable shall be of reputed make. At the top there shall be weather proof junction box to terminate the trailing cable. Connections from the top junction box to the individual luminaries shall be made by using 3 core 1.5 sq. mm flexible PVC cables of reputed make. The system shall have in-built facilities for testing the luminaries while in lowered position.  Also, suitable provision shall be made at the base compartment of the mast to facilitate the operation of internally mounted, electrically operated power tool for raising and lowering of the lantern carriage assembly.  The trailing cables of the lantern carriage rings shall be terminated by means of specially designed, metal clad, multipoint plug and socket provided in the base compartment to enable easy disconnection when required.

- Power Tool for the Winch:

A suitable, high-powered, electrically driven, internally mounted power tool, with manual over ride shall be supplied for the raising and lowering of the lantern carriage for maintenance purposes. The speed of the power tool shall be to suit the system. The power tool shall be single speed, provided with a motor of the required rating.  The power tool shall be supplied complete with a suitable control arrangement so that the operation of the mast can be done at a safe distance. The capacity and speed of the electric motor used in the power tool shall be suitable for the lifting of the design load installed on the lantern carriage.

The power tool mounting shall be so designed that it shall be not only self supporting but also aligns the power tool perfectly with respect to the winch spindle during  the operations. Also, a handle for the manual operation of the winches in case of problems with the electrically operated tool, shall be provided. There shall be a separate torque limiting device to protect the wire ropes from over stretching. It shall be mechanical with suitable load adjusting device. The torque limiter shall trip the load   when it exceeds the adjusted limits. There shall be suitable provision for warning the operator once the load is tripped off. The torque limiter is a requirement as per the relevant standards in view of the overall safety of the system. Each mast shall have its own power tool motor.

- Lightning Finial

One number heavy duty hot dip galvanised lighting finial shall be provided for each mast. The lightning finial shall be minimum 1.2 M in length and shall be provided at the centre of the head frame. It shall be bolted solidly to the head frame to get a direct conducting path to the earth through the mast. The lightning finial shall not be provided on the lantern carriage under any circumstances in view of safety of the system.

- Aviation Obstruction Lights:

Medium intensity LED aviation obstruction light similar  to neon spiral type fitted in a weather- proof box on body unit of Aluminium  alloy  shall    be supplied.  The cover of the light will be glass with rubber  gasket   (IP55 protection). High Luminosity flashing red light emitting diodes having life of 11 years. Power consumption 10 to 15 Watts, 230V AC, 50HZ, 90 candela. LED#s are mounted on fire retardant epoxy printed circuit board in five series - parallel circuits.- 1 Set

Make- Binay  Opto Electonics  Pvt. Ltd./Bajaj Electricals Ltd/ Philips.

- Lightning protection

Lightning protection shall be provided on the top of the high mast. Lightening arrester shall be connected to 2nos. of Earth electrode.

- Earthing Terminals:

Suitable earth terminal using 12 mm diameter stainless steel bolts shall be provided at a convenient location on the base of the Mast, for lightning and electrical earthing of the mast.

- Earthing System

The mast shall be provided with lightning protection system comprising of an Earthing system as follows:

40 mmdia, 2.5 meters Long G.I Pipe with bricks enclosures and cover - 4Nos.

35mm X 6mm G.L straps for interconnection of stud at mast

2nos.earh electrodes for lightening arrester and 2Nos. earth  electrodes for earthing system of high mast lighting system.

- Feeder Pillar:

Each mast shall be provided with a feeder pillar fabricated out of 14 SWG CRCA sheet and finished with two coates of red oxide primer and Gray enamel paint of shade 631 of IS-5.  The feeder pillar shall comprise of incoming MCB Isolator, Copper wiring, suitable timer and contactor to switch on the luminaries at a pre-set time. There shall be suitable control arrangement to change the direction of rotation of the power tool-motor. Feeder pillar shall be mounted on suitable foundation near to the mast.

At this feeder pillar a space is required for separate CSPDCL metering arrangement.

- Incoming Power Cable

A cable of size 4 x 16 sq.mm Aluminium conductor, Armoured cable for power supply (max 10 M) and 3 x 2.5 sq.mm Copper conductor Armoured cable for motor supply shall be provided from feeder pillar to the base compartment of the high mast.  Cable shall be taken to the base compartment of the high mast through the provision made in the foundation.

- Applicable standards :

The following standards will be applicable :

(a) IS 875 (Part 3) – 1987 updated till date : Code of practice for Design loads (other than earth quakes) for building and structures.

(b) BE EN 10025/DIN 17100 : Grades of M.S. Plates.

(c) BS ISO 1461 : Galvanising , (d)BS 5135 / AWS : Welding

(d) TR No. 7 1996 of ILE, UK : Specifications for Mast and foundation.

- TOOL BOX:

A tool box of sheet steel containing a set of general and special purpose tools is  to be supplied along with high mast.

- TECHNICAL SPECIFICATION FOR EARTHING SYSTEM

- EARTHING SYSTEM

All equipment of the lighting system shall be earthed as per relevant Indian Standards. General specifications of earthing for pole, SLFP & equipments are given below.

Each pole shall be earthed using 1 no. 40mm dia., 3 m long  GI Pipe. The connections between the earthing stud inside pole and the electrode shall be done with 25X6 GI strips.

SLFPs and equipments each shall be earthed with 2 nos. - 40mm dia., 3 m  long GI pipe. The connections between the earthing stud and the electrode shall be done with 25X6 GI strips.

- Specifications for Earthing

The entire earthing of the equipment to be supplied and erected shall be carried out strictly in accordance with the latest IS-3043 / IER/ IEC 60034.

    - Earth electrodes for L.T. system: - Main earth electrodes 40 mm dia 2.9 mm thick 3.00 m long GI pipe providing with 12 mm dia through holes, 150 mm intervals staggered along with the main electrode, the main electrode shall be coupled to a 19 mm dia GI pipe of suitable of length at one end through a reducing socket of size 40 mm x 19 mm size. The other end of 19 mm dia GI pipe is required to be provided with a funnel with wire mesh, GI check nuts, GI nut washers etc.

    - A suitable pit of 200 mm diameter to be dug all round the main electrode, the pit shall be filled with alternate layer of coal or charcoal and salt in 150 mm thick layers up to the entire length of the main electrode.

    - An inspection chamber of size 300 mm x 300 mm x 300 mm size in CC 1:3:6 with 150 mm thick side walls, 100 mm thick at bottom shall be provided. The inspection chamber shall be covered with MS or CI frame and cover. The cover shall be hinged to the frame and provided with padlocking arrangements. Inspection chamber frame and cover shall be finished with anticorrosive primer and numbered.

    - fault clearing time for sizing earthing conductor shall be as per latest IS / I.E. rules and plant earthing system shall be designed such that overall earthing resistance is less than one ohm. The Bidder shall measure the soil resistivity at site.

    - Testing of Earthing System: Employer may ask to carry out earth / continuity tests, earth resistance measurements and other tests in presence of him which in his opinion are necessary to prove that the system is in accordance with design, specifications, Indian Code of Practice and Indian Electricity Rules. Contractor shall have to bear the cost of all such tests.

    - The street lighting poles shall be earthed with 40 mm dia 3 mtr. long GI pipe or 20 mm dia GI rod buried in earth with necessary double GI earthing No. 8 SWG complete erected and connected to the street light poles.

    - For earthing of the feeder pillars, one no. earth pit shall be provided for each feeder pillar. The earth pit shall be complete with 40 mm dia, 3 mtr. Long earth pipe, watering pipe, wire mesh, funnel charcoal, slat etc. as per IS 3043. the feeder pillar shall be earthed at two points from the pit with 8 SWG GI wires.

- LT XLPE POWER CABLES :

The scope of this specifications covers design, manufacturer, inspection, testing at works, packing and forwarding of 1100 V grade LT XLPE Power cables

- STANDARDS :

The cables offered shall conform to the latest revision of relevant Indian Standard Specifications.   Some of these standards are list below :

| Sr.No | Indian standard specification no. | Title |
| --- | --- | --- |
| 1 | 7098 | XLPE insulated electrical cables for working voltages upto 1100 V |
| 2 | 8130 | Conductors for insulated electric cable and flexible cords. |
| 3 | 5831 | PVC insulation & sheath of electric cables. |
| 4 | 3975 | Mild steel wires, strips and tapes for armouring of cables. |
| 5 | 2633 | Methods of testing weight, uniformity of coating, thickness on hot dip galvanized articles |
| 6 | 3961 | Recommended current rating for cables, PVC insulated and PVC sheathed. |
| 7 | 1753 | Aluminium conductors for insulators cables. |

- PRINCIPAL PARAMETERS

4.02.1	 the LT XLPE power cables shall be used outdoors, directly buried through  pipes / duct for street lighting works  and its power supply arrangement.

4.02.2	The cable shall meet the requirements of IS specifications listed above and the general technical requirement detailed below :

- GENERAL TECHNICAL REQUIREMENT :

4.03.1	The cables shall be brand new.   It shall be suitable for laying through double wall corrugated high density polyethylene pipes.

4.03.2	 All the LT XLPE power cables shall be 1100 V grade with aluminium conductor, XLPE insulated, inner sheathed, armoured and over all PVC sheathed.

4.03.3 	The construction of the conductors shall be stranded for aluminium cable. Conductors of nominal area of 25 sq.m shall be circular.   Those above may be circular oval shaped.

4.04 	The core insulation shall be with XLPE compound applied over the conductor by extrusion duly and shall conform to the type A compound of IS 5831.

4.05 	The inner sheath shall be applied over the laid up cores by extrusion and shall be of XLPE confirming to the requirements of type ST1 PVC compound.   The extruded inner sheath shall be of uniform thickness of 0.5 mm upto 16 sq.mm 0.8 mm upto 120 sq.mm. & 1.0 mm above 120 sq.mm conductor size.

4.06 	The armouring shall be by single round galvanized steel wires for cable diameter upto 13 mm and galvanized steel strips for cables diameters above 13 mm.

4.07 	The outer sheath of the cables shall be applied by extrusion and shall be of PVC compound.  Suitable chemicals shall be added to the PVC compound of the outer sheath to protect the cables against rodent and termite attack.

  - The dimensions of the insulation armour and outer sheath material shall be governed by IS specification.

- CABLE LAYING :

This is to define the requirements for the installation, testing and  commissioning of the cabling system.

5.01 	CABLE LAYING :

The cable laying shall be from supply point to the feeder pillar panel and from feeder pillar panel to street lighting poles.    The cable from supply point up to the feeder pillar and from feeder pillars to the lighting poles shall be laid underground through suitable size double wall corrugated high density polyethylene pipes.    The trench shall be at least 0.9 mtr. Deep and 0.4 mtr. Wide.   At road crossings, the cable shall be laid in 100 mm dia RCC hume pipe of NP-2 class.   The trench shall be carried in all type of soils  hard murum/ hard rock / soft soil / Tar road / WBM road, which is included in the slope of work.   No extra payment will be provided on account of any change in site conditions.  Cables as far as possible shall be laid in complete, uncut lengths from one termination to the other. All cables will be identified close to their termination point by cable numbers as per cable schedule.   Cable numbers will be punched on aluminium straps (2mm thick) securely fastened to the cable and wrapped around it.

Alternatively cables tags shall be circular in construction to which cable numbers can be conveniently punched.   Each underground cable shall be provided will identity tags of lead securely fastened every 30 m. of its underground length with atleast one tag at each end before the cables enters the ground.   In unpaved area, cable trenches shall be identified by means of markers as per standard drawing.   These posts shall be placed at location of changes in the direction of cables and at intervals of not more than 30 m. and at cable joint locations.  All temporary ends of cables must be protected against dirt and moisture to prevent damage to the insulation.

5.02 	TERMINATION :

All XLPE cables upto 1.1 KV grade shall be terminated at the equipments by means of compression type cable glands of aluminium.   They shall have a screwed nipple with conduit electrical threads and check nut.  Cable leads shall be terminated at the equipment terminals by means of crimped type solder less connectors as manufactured by M/s Dowel Electro Works or approved equivalent.

5.03 	TESTING :

Before energizing, the insulation resistance of every circuit shall be measured from phase to phase and from phase to ground.

- Specification of HDPE Pipes:

6.01	The DWC high density polyethylene pipe having corrugation on outer wall and plain inner wall shall confirm to IS-14930 part – I & II amended upto date.

6.02	The pipe shall be ISI marked.

6.03	Contractor has to arrange inspection of pipe at manufacturer’s premises to carry out necessary tests contained in IS-14930 part-I & II (compression test, impact test, banding test etc.).

6.04	Job includes (laying of pipe item No. 1/SH 4) accessories like HDPE snap fit coupler with required No. of neoprene `O’ rings in order to make water/damp proof joint.

6.05	Contractor has to produce test report of anti rodent test, toxicity test of pipe from Govt. approved test house.

- STREET LIGHTING FEEDER PILLAR (SLFP)

- The contractor shall have to get the control panels fabricated from the vendor having type test  	certificate from CPRI for 31 MVA short circuit rating upto 400 amp. for cubical panels.  The copy of 	the type test certificate shall also have to be produced failing which feeder pillar shall not be 	accepted.

- Angle iron legs shall be suitably shaped at the bottom for anchoring in concrete base.

- SLFP shall be suitable for 415 V, 3 phase, 4 wire, 50 Hz supply and shall be outdoor type with 	canopy and shall be free standing floor type.

- SLFP shall be provided with incoming & outgoing MCCB / MCB of appropriate rating and in 	desired quantity depending on total no. of circuits in use. Outgoing shall have at least one spare 	circuit all the time.

- SLFP shall be made up of CRCA sheet steel and shall be dust and vermin proof providing a 	degree of protection of IP 55. The thickness of sheet steel enclosures shall be 2 mm minimum.

- The feeder pillars shall be provided with ventilation window covered with wire net in  double fold 	from inside.  The window shall be provided on both the side panels of feeder pillars.

- The feeder pillars shall be provided  with a danger notice  plate as per IS standard.

- Interconnections of the various mountings on the feeder pillar shall be done using PVC  insulated 	conductors, or solid strips with  PVC taping/sleeving of appropriate sizes.  Termination shall be 	made such that local heating is avoided, suitable lugs shall be used for connections.

- Busbars will be made up of aluminium, colour coded for easy identification and of appropriate size.

- Doors shall be provided with all round neoprene gaskets. The incomer switchgear shall have interlocking mechanism so as to prevent opening of the door when the switch is ON and to prevent closing of the switch when the door is not fully closed. However, a device for bypassing the door interlock shall be provided to enable the operation of the switch with the door open, when necessary, for examination / maintenance.

- All accessible live connection/metals shall be shrouded and it shall be possible to change individual fuses, switches, from the front of the boards/panels without any danger of contact with live parts.

- Adequate interior cabling space and suitable removable cable gland plate (min. 3 mm thickness) plates shall be provided for bottom entry of cables through glands. Necessary number of glands to suit the required cable sizes shall be provided. Cable glands shall be double compression type made of chrome-plated brass.

- Every SLFP will have LED type ‘SUPPLY ON” indicating lamps. Indicating lamps shall be of the clustered LED type and low watt consumption. Lamps shall be provided with series resistors.

- Earth bus of 50x6 GI flat with zinc plated bolts and nuts shall be provided in the bottom of the panel.

- The SLFP shall be provided with individual labels with equipment designation  / rating. Also the boards shall be provided on the front with a label engraved with the designation of the SLFP. Labels shall be made of non-rusting metal or 3 ply lamicoid or engraved PVC.

- Internal wiring of the panel shall be done using flexible copper cables of appropriate sizes. All the wires shall be numbered and ferrules shall be provided for easy identification.

- Proper clip-on stud type terminals of appropriate rating shall be provided for termination of incoming as well as outgoing cable  inside the SLFP.

- Inside the door of lighting panels a single line circuit diagram / description shall be fixed for ready reference.

- Painting: All sheet steel enclosures of panels will be chemically cleaned rinsed, phosphated & dried. After the treatment steel surfaces will be given two coats of primer & finished grey enamel paint or powder coating of shade 631 of IS - 5. Coating thickness shall be minimum 50 microns.

- CABLES TAGS AND MARKERS

- Each cable and conduit run shall be tagged with numbers that appear in the cables and conduit schedule.

- The tag shall be of aluminum with the number punched on it and securely attached to the cable conduit by not less than two turns of 20 SWG GI wire conforming to IS: 280. Cable tags shall be of rectangular shape for power cables and of circular shape for control cables.

- Location of cables laid directly underground shall be clearly indicated with cable marker made of galvanized iron plate.

- Location of underground cable joints shall be indicated with cable marker with an additional inscription “Cable Joint”.

- The marker shall project 150 mm above ground and shall be spaced at analysis interval 30 metres and at every change in direction. They shall also be located on both sides of road and drain crossings.

- Cable tags shall be provided on all cables at each end (just before entering the equipment enclosure), on both sides of a wall or floor crossing and on each duct/ conduit entry. Cable tags shall be provided inside the switchgear, motor control centers, control and relay panels, etc., wherever required for cable identification, such as where a number of cables enter together through a gland plate.

- The price of cable tags and markers shall be included in the installation rates for cables/ conduits quoted by the contractor.

- Specific requirements for cabling for cabling, wiring, ferrules as covered in respective equipment section shall also be complied with.

- CABLE LUGS

Solder less crimping of terminals shall be done by using corrosion inhibitory compound. The cable lugs shall suit the type of terminals provided. Crimping tool used shall be of approved design and make.

- CABLE TERMINATIONS AND CONNECTIONS

- The termination and connection of cables shall be done strictly in accordance with cable and termination kit manufacturer’s instructions, drawing and/ or as directed by the Owner.

- The work shall include all clamping, fittings, fixing, plumbing, soldering, drilling, cutting, taping, heat shrinking (where applicable), connecting to cable terminal, shorting and grounding as required to complete the job.

- The equipment will be generally provided with un-drilled gland plates for cables/ conduit entry. The Contractor shall be responsible for drilling of gland plates, painting, and touching up. Holes shall not be made by gas cutting.

- The Contractor shall tag/ferrule the control cable cores at all terminations, as instructed by the Owner. In panels where a large number of cables are to be terminated and cable identification may be difficult, each core ferrule may include the complete cable number as well. Spare cores shall be similarly tagged with cable numbers and coiled up.

- All cable entry points shall be sealed and made vermin and dust proof. Unused openings shall be effectively closed.

- If the cable-end box or terminal enclosure provided on the equipment is found unsuitable and requires modification, the same shall be carried out by the Contractor with the approval of the Owner.

- MCCB

The MCCBs provided in these boxes shall conform in all respects to the relevant IS: 2516 (Pt-I&II)/1977 and REC specification No.18/1981 (revised) or its latest revision as applicable.

  - REQUIREMENT OF MCCBs:

The moulded case circuit breakers should comprise of a switching mechanism, an effective extinguishing device and a tripping unit contained in a compact moulded case cover made of high strength, heat resistance and flame retardant thermo-insulating materials. They should comprise of a spring assisted quick make/ quick break type independent manual trip free mechanism rendering it easy to manually operate the MCCBs and capable of clearly indicating “TRIPPED”, “ON” AND “OFF” positions from the position of the operating handle. The contact tips should be made of a suitable alloy having high arc resistance and a long electrical and mechanical life needing no replacement. The breakers should be designed with a common trip bar to break and make all the three phase together even when fault occurs on any of the phases. The breakers should provide protection against sustained overloads and short circuits through thermal-magnetic/ fully magnetic releases. These MCCBs along with terminal blocks are intended to be housed in the distribution boxes made out of sheet steel of 2mm gauge. The assembly of the MCCBs and the terminal blocks should be compact, reliable from operation point of view and safe to the operating personnel. As already mentioned earlier, the MCCBs should be fully maintenance free.

  - TECHNICAL PARTICULARS OF MCCBs:

The LT MCCBs should have inverse current/ time characteristics suitable for protection of 315KVA, 11.0.4KV Distribution Transformers against sustained over-loads and short circuits for following operating conditions:-

| i | Rated Operating Voltage | 3 Phase 415 Volts AC 50 cycles with neutral solidly grounded system |
| --- | --- | --- |
|  | Rating | 100 Amps |
| iii | No. of Poles | 4 |
| iv | Duty | Un-interrupted |
| v | Maximum ambient temperature | 47oC in shade |
| vi | Minimum ambient temperature | 4oC in shade |
| vii | Average altitude | A maximum of 1000 meter |
| viii | Maximum humidity | Frequently approaches saturation point |

  - TIME/CURRENT CHARACTERISTICS:

The circuit breakers shall have time/current characteristics suitable for following operating conditions:

| Multiple of normal current rating | Tripping time |
| --- | --- |
| 1.1 times | After 4 hours |
| 1.2 times | Less than 50 minutes |
| 1.3 times | Less than 30 minutes |
| 1.4 times | Less than 10 minutes |
| 2.5 times | Less than 1 minute |
| 6 times | Less than 40 mili-seconds |
| 12 times | Less than 40 mili-seconds |

Time/ Current characteristic of the Circuit Breaker (MCCB) shall be tested in accordance with Clause-7.7.2.3 (b) (2) of IS: 2516-(Pt-I&II) Sec.I/1977 and the test shall be made with all the three phases loaded.

For time/ current characteristic, the reference calibration temperature of the MCCBs shall be 40oC and durance, if any, upto 50oC operating temperature in the enclosure shall not exceed 10% of the value indicated above in Clause (I) above.

The MCCBs shall be calibrated and adjusted in the factory itself for the desired time/ current characteristic.

The MCCB should have the following maximum resetting time under overload & short circuit conditions:-

- Overload conditions   		-	3 minutes

- Short Circuit conditions		-	Instantaneous

  - RATED SHORT CIRCUIT BREAKING CAPACITY:

The rated short circuit breaking capacity of the MCCBs shall be35 KA-

The short circuit breaking capacity test as specified above shall be based on short circuit tests carried out at 0.4 Power Factor (lagging). For the purpose of these tests, the following operating sequence shall be followed: -

Break-3 minutes itnerval-Make-Break-3 minutes interval-Make-Break.

- LED Street Lighting Luminaries

12.1	 General Requirement

Supply of LED streetlight Luminaire with power consumption of not more than 210W for 35 meter pole to pole spacing and 160 W for 28/30 meter pole to pole spacing complete with single piece high pressure die cast aluminum housing with supplier wordmark / name engraved / emborssing on the die cast housing to allow traceability till life of fixture (Stickering / printing is not acceptable) and adhering to the following specifications:

- The housing should be single piece high pressure die cast should be open-able at the pole top using clips and no screws should be used to fix cover with housing

- The luminaire should be suitable for side-entry road light poles with a typical pole diameter of 40-60mm.

- The fixture shall be designed so as to have lumen maintenance of at least 70% at the end of 50,000 hours ( L70) and L90 of > 1,00,000 hour at design temperature of 35 degree C.

- The luminaire should be operable with auto adjustable 120 – 300 V supply Voltage using the same driver.

- Power Factor of the electronic driver should be at least >0.95 and with THD<15%,

- The luminaire should throw the perfect amount of uniform light with exactly the desired intensity along with better light control.

- The luminaire to be provided with heat resistant toughened curved glass.

- The Luminaire shall employ individual optical lens for the each of the LED’ to ensure better uniformity of light distribution.

- The fixture should be impact resistant with suitable protection by using cover for driver and LED’s, confirming to minimum IK08 impact resistance specifications.

- The fixture should have double-wall construction with silicone gasket and with breather designed for IP66 ingress protection without using any glue to prevent breakdown of the water and dust proof seal

- Heat dissipation should be managed through a built-in external heat-sink. The luminaire shall deliver more than 85 Lumen/Watt, (+5%) Color Rendering Index of minimum 70(+5%) with cool white light output.

- The luminaire should be provided with option of dimming function to enhance energy saving if required.

- Max LED Junction Temperature 150 Deg C rating for better capacity to handle heat.

- Make of LED’: Philips, Cree, Nichia, and Osram.

  - Electrical Specification

|  | Electrical specifications |  |
| --- | --- | --- |
|  | Electrical ratings of the proposed luminaire product for the following criteria: |  |
| i) | Voltage range or rating: on single phase | 120 V to 300 V |
| ii) | System lumen’s per watt (+/-5%) | >85 |
| iii) | Frequency range (+/-5) | 50Hz |
| iv) | Power factor: | >/= 95 |
| vi) | Colour temperature | >/=5000K to </= 7000 |
| vii) | CRI | >70% |
| viii) | Life Expectency | 50000 hrs with 70% Lumens |
| ix) | Total Input wattage to the fittings including driver losses | </=215 W ± 5%. |
|  | For 28/30 meter spacing | <=160 Watt |
|  | For 35 meter spacing | </=215 Watt |
| x) | Protection level | IP66 |
|  | Surge Protection : Differential level | 4.5 KV |
|  | Electrical Insulation class | CLASS I |
| Xi) | Total Harmonic Distortion | < 15% |
| Xii) | Operating temperature | -5 Deg to + 35 Deg C |

12.3	Applicable Standards:

- LED must comply all the parameters of  IES LM 80(Equivalent Indian Standard – IS 16105 – 2011) .

- LED must comply all the parameters of  IES LM 79-08(Equivalent Indian Standard – IS 16106 – 2011).

- The luminaire shall conform to IEC 60598 standard, CLASS I, For Luminous efficiency and light output, Photometry Test of the Luminair IS 10322 TC, IEC60598 TC.

- The driver should comply with

  - EN61347-1: general and safety requirements

  - EN61347-2-13: particular requirements for DC or AC supplied electronic control gear for LED modules

  - EN62384: DC or AC supplied electronic control gear for LED   modules. Performance requirements

  - EN 61000-3-2 Limits for harmonic currents emissions

  - EN 55015 : Limits for Radio disturbance characteristics of electrical equipements

- Lighting level should be as per the requirement of IS 1944: PART II and the prevalent standards.

12.4	Following data must be submitted along with the technical bid:

- Life of LED, colour characteristics and other relevant details to be supported by IES LM 80 (Equivalent Indian Standard – IS 16105 – 2011) report and the the LED life should be projected for 6000 burning hours as per IES TM21-2011. The LM80 certification should be from the manufacturer of LED. The Luminaire supplier must  submit

(a ) letter from the manufacturer of LED that LED used are from his manufacture.

( b ) LED used is the same one as certified by LM 80 reports.

- Measurement of Luminous flux should be carried out at following temperature –

at 35 ᵒC, 85 ᵒC and 105 ᵒC.

- Luminaire Photometric Measurement Data ( Luminaire Efficacy, Light Intensity Distribution Diagram, Co-efficient of Utilization curve, Electrical parameters ( Test Voltage, Current, Wattage, Power Factor, THD) and efficiency of driver are to be certified by measurements as per IES LM79-08 (Equivalent Indian Standard IS 16106-2011). The test report should be generated by the laboratory of the manufacturer or NABL accredited Labs. The manufactures lab also have NABL accredition.

- Relevant LED and Luminaire data sheets and Type test certificates indicating compliance to the technical specifications / standards.

- Lighting design report for the Mock up test conditions indicating the Average illuminance (lux), uniformity, maximum and minimum values. Polar curve of the light fitting indicating the light distribution capability of luminaire should also be attached. Authorization certificate in case the bidder is not a manufacturer.

- Mounting Instruction sheets.

- Make of LED, Luminaire and Electronic Driver used.

12.5 	Wiring of the luminaries

The wires for connection from terminal plate of the pole to the fixtures shall be 1100 V, minimum 3Cx2.5 sq mm PVC insulated, unarmoured having flexible copper conductors. The wires shall conform to the applicable IS.

12.6	TEST:

The following routine tests shall be conducted as per the relevant Indian Standards

a) 	Insulation resistance of each fixture shall be tested at 500 V.D.C. & the insulation resistances so measured shall not be less than 2 mega ohms between all current carrying parts and ground.

b) 	Each fixture complete with its proper lamp/lamps shall be shown to operate satisfactorily at its normal voltage and frequency.

c) 	Each fixture shall be examined visually to ensure that it is complete in all respects and satisfactorily finished.

d) 	Type and routine test certificates shall be submitted for tests conducted as per relevant standard for the fixture, accessories and work.

13.   DISTRIBUTION TRANSFORMERS

13.01.	Scope

The specification covers the design, manufacture, testing and inspection before dispatch and delivery of distribution transformers at Naya Raipur. The specification covers oil immersed, naturally air cooled (type ONAN), outdoor type, three star rating, three phase, 50 Hz, 11/0.433 KV step down distribution transformers of capacity25 &  63 KVA.

13.02. System Particulars:-

The transformers shall be suitable for outdoor installation with following system particulars and they should be suitable for service under fluctuations in supply voltage as permissible under Indian Electricity Rules

13.2.1 	Nominal System Voltage 			 	: 11 kV

13.2.2 	Corresponding Highest System Voltage			: 12 kV

13.2.3 	Neutral earthing 					: Solidly earthed

13.2.4	Frequency						: 50 Hz with ±3 % tolerance

13.2.5 	Number of Phase					: 3

13.03. 	Applicable Standards

13.3.1	 The design, manufacture and performance of the equipment shall comply with all currently applicable statutes, regulations and safety codes. Nothing in this specification shall be construed to relieve the bidder off his responsibilities.

13.3.2 	The Distribution Transformers shall conform to IS: 2026 as amended up to date or other International Standards for equal or better performance. Unless otherwise modified in this specification the Distribution Transformers shall comply with the Indian Standard Specification IS 2026 latest.

13.3.3	Unless otherwise specified, the equipment offered shall conform to amended up to date Indian, IEC, British or U.S.A. Standards and in particular, to the following:-

| a. | IS 2026(Part I,II,IV)/1997,(Part-III)/1981, (Part-V)/ 1994 | Power Transformer |
| --- | --- | --- |
| b. | IS: 1180/1989 (Part-1& Part-2) | Outdoor type, Three phase distribution transformers up to and including 100 kVA, 11KV |
| c. | IS:335/1993(fourth revision) | New insulating oil- Specification |
| D | IS:2099/1986, IS: 7421-1988, IS:3347 (Part-I /Sec-2)-1979, IS:3347 (Part-I /Sec-1)-1982 amended up to date | Bushing |
| E | IS 5 | Colours for ready mixed paints and enamels. |
| f. | IS 13730 (Part-27)1996 | Specification for particular types of winding wires. |
| g. | CBIP Publication No.295:2006 | Manual on transformers |

13.3.4 	In case of conflict arising out due to variations between the applicable standard and the standards specified herein the provisions of this specification should prevail.

13.04.	Climatic Conditions

(i)	 Peak Outdoor temperature 		: 50 0 C Minimum (50 0 C+40 0 C)

(ii)	Maximum oil temperature		: (50 0 C+35 0 C)

: 850C under max. temperature & max load    						   condition attainable.

(iii)	Maximum relative humidity		: 95% (sometime approaches saturation

point).

(iv)	Minimum relative humidity		: 10%

(v)	Average No. of thunderstorm		: 40 days

days per annum.

(vi)	Average number of rainy days   	: 90 days

(vii)	Number of months of tropical		: 3 months

monsoon conditions.

(viii)	Average annual rainfall		: 125 cm.

(ix)	Wing pressure			: 100 Kg/m2

(x)	Altitudes not exceeding		: 1000 meters.

13.05. 	Specific Technical requirement:

13.5.1 	Standard kVA Ratings:-The standard ratings for transformer shall be 63 kVA.

13.5.2 	Nominal voltage ratings:

Primary voltage		: 11 kV

Secondary voltage	: 0.433 kV

13.5.3 	Winding connections:-

i. H.V. Winding 		: Delta (A)

ii. L.V. Winding 		: Star (Y)

The neutral of the L.V. winding shall be brought out to a separate insulated terminal. The voltage 	group shall be Dyn-11.

13.5.4 Temperature Rise:

a. 	The temperature rise for top oil over an ambient temperature of 50° C should be 35 °C maximum measured by thermometer in accordance with IS 2026.

b. 	Temperature rise for winding over an ambient temperature of 50° C should be 40° C maximum (measured by resistance method in accordance with IS 2026.

Bids not meeting the above limits of temperature rise will be treated as non responsive.

The transformer shall be capable of giving continuous rated output without exceeding the specified temperature rise.

13.5.5 	No load voltage ratio:-

The no load voltage ratio shall be 11000/433 Volts.

13.06. 	Taps

No tapings shall be provided for transformers upto 100kVA rating.

  - Design & construction:

13.7.1	Core

i. 	The core shall be stacked type. The core shall be of high grade cold rolled grain oriented (C.R.G.O) annealed steel lamination having low loss and good grain properties, coated with hot oil proof insulation, and bolted together to the frames firmly to prevent vibration or noise. All core clamping bolts shall be effectively insulated. The complete design of core must ensure permanency of the core losses with continuous working of the transformers.

ii. 	The grade of core laminations shall be M4 or better. The value of the flux density allowed in the design and grade of lamination used shall be clearly stated.

The successful bidder shall be required to submit the manufacturer’s test report showing the Watt loss per Kg and the thickness of the core lamination, to ascertain the quality of core materials. The purchaser reserves the right to get sample of the core material tested at any Govt. recognized laboratory.

(iii)	The transformer core shall not be saturated for any value of v/f ratio to the extent of 112.5% of the rated value of V/f ratio (i.e. 11 KV/50 due to combined effect of voltage and frequency) up to 12.5% without injurious heating at full load condition and should not get saturated. The supplier shall furnish necessary design data in support of this situation.

(iv) 	Flux density should not be more than 1.55 Tesla for CRGO transformers at the rated voltage and frequency. The value of the flux density allowed in the design shall be clearly stated in the offer along with graph.

No load current at rated voltage and at 112.5% of rated voltage for 25 KVA rating shall not exceed the % (percentage) values given below for different types of core:

| KVA Rating | No load current as a percentage of rated full load current |  |
| --- | --- | --- |
|  | At 100 percent Rated Voltage | At 112.5 percent Rated voltage |
| 25 | 3 | 6 |
| 63 | 3 | 6 |

Test for magnetic balance by connecting the LV phase by phase to rated phase voltage and measurement of an, bn, cn voltages will be carried out.

- Details of Core:

| Particulars | Rating in KVA |
| --- | --- |
|  | 25 & 63 |
| No. of steps (Min) for stack core | 5 standard steps |

13.7.2     Winding:-

i. Materials:  Double paper covered / Super enamel covered Aluminium conductor shall be used for HV and LV winding.

ii.  Density: Current density for HV and LV should not be more than 1.6 A / sq.mm for aluminium conductor.

iii. L.V. winding shall be in even layers so that neutral formation will be at top.

13.07.3	Losses:

The total losses at 50% & 100% loading for three phase, three star rating 25, 63 & 100 KVA, 11/0.433 kV transformers at rated voltage, frequency and at 75 deg. Centigrade shall not exceed the values indicated as below:

Note:	Please refer to the Technical Specification for 3 Star Distribution Transformer given by Bureau of Energy Efficiency (the same is enclosed below as a schedule V).

TABLE – 1

| KVA Rating | Voltage Ratio in kilovolts | Losses at 50% loading (Watts) at 750C | Losses at 100% loading (Watts) at 750C |
| --- | --- | --- | --- |
| 25 | 11/0.433 | 210 | 695 |
| 63 | 11/0.433 | 380 | 1250 |

Apart from above, Distribution Transformers should conform to minimum requirements of IS 1180 (Part-I):1989 for no load losses etc.

No positive tolerance shall be allowed in the maximum losses given in the table for both 50% & 100% loading values. Bids with higher losses than the above specified values would be treated as non-responsive. In case the actual loss values exceed the above guaranteed values, the transformers shall be rejected at the risk, cost and responsibility of the supplier.

The values guaranteed in G.T.P. for flux density, no load current at rated voltage, no load current at 112.5% of rated voltage and no load loss at rated voltage shall be individually met.

13.7.4	Insulation material & clearances:

(a) 	Materials – Makes of Electrical grade insulating epoxy dotted craft paper, Pressboard of standard make shall be declared in GTP by the bidder. All spacers, axial wedges/runners used in windings shall be made of pre-compressed pressboard-solid confirming to type B 3.1 of IEC 641-3-2. The test reports for all properties as per relevant I.S. amended up to date shall be submitted during inspection.

(b) 	The minimum electrical clearance between the winding and body of the tank (between inside surface of the tank and outside edge of the windings) should be 30 mm.

(c) 	Minimum external clearances of bushing terminals

| HV | Ph to Ph | 255 mm |
| --- | --- | --- |
|  | Ph to E | 140 mm |
| LV | Ph-to-Ph | 75 mm |
|  | Ph to E | - m |

13.7.5	Impendence value:-

The percentage impendence at 750C shall be 4.5% for transformers (IS tolerance of ± 10%).

    - Tank

    - The transformer tank shall be made up of prime quality MS Sheets of rectangular shape. The transformer tank shall be of robust construction. All joints of tank and fittings should be oil tight and no bulging shall occur during service. The tank design shall be such that the core and windings can be lifted freely. The tank plates shall be of such strength that the complete transformer when filled with oil may be lifted bodily by means of the lifting lugs provided. Tank inside shall be painted by varnish. Top cover plate shall be slightly sloping; approximately 5 to 10 deg. Towards HV bushing and edges of cover plate should be bent downwards so as to avoid entry of water through the cover plate gasket. The width of bend plate shall be 25 mm min. The top cover shall have no cut at point of lifting lug. The rectangular tank shall be fabricated by welding corners.

    - In rectangular shape tanks, horizontal or vertical joints in tank side walls and its bottom or top cover will not be allowed. In addition the cover of the main tank shall be provided with an air release plug.

Side wall thickness			:	3.15 mm. (min.)

Top and bottom plate thickness	:	5 mm. (min.)

    - Reinforced by welded angle 50x50x5 MM on all the outside walls on the edge of tank to form two equal compartments. The permanent deflection is not more than 5mm up to 750 mm length and 6mm up to 1250 mm length when transformer tank without oil is subject to air pressure of 35 KPa above atmospheric pressure for 30 min. Pressure test shall be performed carefully at the time of 1st stage inspection only to confirm the adequacy of reinforcement angle and gauge of the tank.

    - All welding operations to be carried out by MIG process.

    - Lifting lugs: 2 nos. welded heavy duty lifting of MS plate of 8mm thickness suitably reinforced by vertical supporting flat of same thickness as of lug welded edgewise below the lug on the side wall, up to reinforcing angle. They shall be so extended that cutting of bend plate is not required.

    - Pulling lugs: 4 nos. of welded heavy duty pulling lugs of MS plate of 8mm thickness/ pulling holes in the base channel shall be provided to pull the transformer horizontally on width side up-to 100kVA.

    - Top cover fixing bolts: GI nuts bolts of 3/8” dia. with one plain washer shall be used for top cover fixing spaced at 4” apart. 6mm neoprene bonded cork/ nitrile rubber bonded oil resistance gaskets conforming to type B/C IS 4253 Part – II amended up to date will be placed between tank and cover plate.

    - Vertical clearance: The height of the tank shall be such that minimum vertical clearance up to the top cover plate of 120 mm is achieved from top yoke.

    - Cable Terminal Box :  The both HV and LV side cable terminal boxes shall be provided to cover the HV and LV terminals.

13.7.7	Heat Dissipation:

13.7.7.1. 	Heat dissipation by tank walls excluding top and bottom should be 500 W/m2.

13.7.7.2.	Heat Dissipation by fin type radiators of 1.25 mm thickness will be worked out on the basis of manufacturer’s data-sheet. Supplier should submit the calculation sheet.

13.7.7.3.	For 63 KVA transformers, 2 Nos. Radiators shall be provided only on LV Side and shall be of fin type. They should be fixed at right angle to the sides and not diagonally.

13.7.7.4.	Arrangement for studs provided for fixing of HV bushings shall be covered by terminal box.

13.7.8	Conservator:

13.7.8.1	The total volume of conservator shall be such as to contain 10% quantity of the oil. Normally 3% quantity of the total oil will be contained in the conservator. Dimension of the conservator shall be indicated in General arrangement drawing.

13.7.8.2 	Die cast Oil level indicator shall be provided on the side of conservator which will be with fully covered detachable flange with single gasket and tightened with MS Nut/Bolt and will be fixed on the side of rating plate and drain valve.

13.7.8.3 	The pipe from the conservator tank connecting to main tank shall be of 30 mm. internal dia. and shall have a slopping plate so that the oil falling from the pipe shall not fall directly on the active job and shall fall on the side walls only. The pipe should project in the conservator so that its end is approximately 20 mm. above the bottom of the conservator. Thus slopping plate should be fitted such that clearance from the yoke/live part of the tap changer is maintained as prescribed i.e. 120 mm. The conservator shall be provided with a filling hole, with cover. In addition the cover of the main tank shall be provided with an air release plug.

Note:	Transformer shall be supplied complete with first filling of oil.

13.8.0	Breather:

Breather joints will be screwed type. It shall have die-cast Aluminium body. Make of breathers shall be subject to purchaser’s approval. Volume of breather shall be suitable for 500 gm. (minimum) of silica gel (crystel size 6 mm).

13.9	Terminals:

13.9.1 	Brass rods of 12 mm dia for H.T. and L.T. with necessary nuts, check nuts and plain thick tinned washers for 63 & 100 KVA ratings.

13.9.2 	HT/LT bimetallic connectors shall be provided with transformer.

13.10	Bushing & Connections:

For 11 KV side - 12 KV bushing and for 433 volts side 1.1 KV terminal bushing will be used. Bushings of the same voltage class shall be interchangeable. Bushings with plain sheds as per IS: 3347 shall be mounted on side of the tank and not on the top cover.  Only continuous sheet metal pocket shall be provided for mounting of all H.V/L.V. bushings and the same shall not be fixed on pipes. Sheet metal pocket shall be designed in such a way that all HT bushings shall remain parallel and equidistance all through. The inside connections of windings to bushings shall remain within the pocket. Bushings having type tested as per IS:3347 shall only be acceptable.

13.11	Internal connections:

In case of HV winding, all jumpers from windings to bushing shall have cross section larger than the winding conductor (normally 1.5 times). For Aluminium winding L&T, Alkapee Aluminium brazing rods with suitable flux will be used or alternatively joints will be made by using tubular connectors properly crimped at three spots. Aluminium brazing rods to be used for ring forming on other end and nut bolting on HV bushing stud.

LT Star connection will be made by using Aluminium/Copper Flat as per winding material and properly brazed or bolted with the crimped lugs on windings by means of plain or spring washers and lock nuts to the flat.  Other end of the conductor is brazed on “L” shape Aluminium/copper flat and flat nut bolted with neutral bushing stud. ALTERNATIVELY, for 63 & 100kVA ratings all the three terminals of LV windings together with terminals for neutral bushing shall be properly brazed and then covered with Aluminium tubular sleeve of suitable length and cross sectional area duly crimped in order to provide sufficient strength to the joint. The star connection should be wrapped with cotton/paper tape.

Firm connection for LV windings to bushings shall be made by brazing with adequate size of “L” shape flat nut bolted with LV Bushing stud. For delta formation on HV side, copper wire having cross sectional area 1.5 times the winding area should be used. SRBP tube /insulation paper should be used for delta connection and on the portion of HV winding joining to HV bushing.

13.12	Tank base channel:

Tank base channels to be fitted across the length of the transformer as follows:

- For 25, 63 & 100 KVA Transformer - Two channels of 75x40 mm of length 460 mm.

13.13	Terminal Marking Plates and Rating Plates:

The transformers shall be provided with a plate showing the relative physical position of the terminal and their markings engraved on it. The transformers shall be provided with non-detachable rating plate of Aluminium anodized material fitted in a visible position, furnishing the information as specified in IS:2026. The rating plate shall be embossed/ engraved type but not printed type. The relative position of tapping switch and corresponding voltages may also be shown on the rating plate.

Further, MS plate of size 125x125 mm be got welded on width side of the transformer on stiffener angle. On this plate Name of firm, order No. & Date, Rating, serial number and Date of dispatch should be engraved. Labeling shall be done as per BEE guidelines.

13.14	Fittings:

The fittings on the transformers shall be as under:

| 1 | Rating and diagram plate | 1 no. |
| --- | --- | --- |
| 2 | Earthing terminals with crimping lugs. | 2 nos. |
| 3 | Lifting lugs | 2 nos. (for tank) |
| 4 | Thermometer pocket | 1 no. |
| 5 | Oil Indicator on tank | 1 no. |
| 6 | Platform mounting channel with suitable holes | 2 nos |
| 7 | HT & LT bushing | 3 nos. of 12 kV HT bushing for 11 kV and 4 nos. of LT bushing (1.1 kV) shall be provided. Each bushing (HV & LV) should be provided with 3 nos. of brass nuts and 2 plain brass washer. |
| 8 | Pulling lugs | 4 nos |
| 9 | Aluminium die cast silica gel 1 No. breather 500 gms. Capacity | 1 no. |
| 10 | Top cover lifting lugs | 2 nos. |
| 11 | Bimetallic connectors to be fitted on the stud | HV: 3 nos. LV: 4 nos. |
| 12 | Radiators | 1 no. for 25KVA/2 nos. for 63& 100KVA |
| 13 | Oil level gauge indicating three position of oil marked as below:-Minimum(-)50C, 300C Maximum 980C | 1 no |
| 14 | Conservator | 1 no. |
| 15 | Cable Terminal Box | 1 for HV Side - for LV side |

13.15  	Transformer Oil:

The transformer shall be supplied complete with first filling of oil and the same shall comply with IS: 335-1983 with latest version thereof with ageing characteristics specified. These characteristics are shown in Schedule-II(C). Type tests certificate of oil being used shall be produced at the time of inspection.

13.16	Tests & Test Certificates

The following routine tests and type tests are required to be carried out on the transformers.

13.16.1	Routine Tests:

Before dispatch, each of completely assembled transformer shall be subjected at the manufacturers works to the following routine tests in accordance with the details specified in IS: 2026:

- Measurement of winding resistances.

- Ratio, polarity and phase relationships.

- Impedance voltage.

- No load losses and no load current.

- Load losses.

- Insulation resistance.

- Separate source voltages withstand.

- Induced over voltage withstand.

- Vacuum test.

13.16.2	Type Test:

In addition to the routine tests as above the following type tests shall be carried out on the transformers in accordance with IS: 2026/1977 as amended from time to time:

- Lightening impulse tests.

- Temperature rise test.

- Short circuit test.

The suppliers may carefully note following specific requirements of short circuit, impulse voltage and temperature rise tests:

The Company intents to procure transformers designed and successfully tested for short circuit and impulse test. It may also be noted that the Company reserves the right to conduct any of the above type tests in accordance with the IS, afresh on each ordered rating at Company’s cost, even if the transformers of the same rating and similar design are already tested. This test shall be carried out on a transformer to be selected by the Company either at their works - when they are offered in a lot for supplies or random sample unit from the supplies already made to Company’s Area Stores. After conducting short circuit test, healthiness of active parts shall be checked by un-tanking the transformer. The findings and conclusion of these tests shall be binding on the supplier.

In case the transformer does not pass in either of the tests and if the active part details are not found to be in line with the design tested and approved, the following punitive measures shall be taken:

(i) 	5% payment of the bill for the supplies already made will be recovered by the Company.

(ii) 	For transformers already supplied, the guarantee period shall stand twice the normal guarantee period. The period of performance Security Deposit shall be suitably extended to cover the extended guarantee period.

(iii) 	Further, supply of balance quantity of transformers will not be accepted by the Company, till another transformer from the manufactured batch is satisfactorily tested (OR transformers are modified according to the tested design) for both tests at your cost and consequent to this, if there is any delay in executing the order, the same shall be to your account. Company reserves the right to take action as per terms and conditions of the order.

(iv) 	The test charges shall be borne by the firm. Please note that if the terms and conditions detailed above regarding short circuit withstand test & impulse voltage test on transformers and procedure for these tests are not accepted by you in full, action will be taken as deemed fit as per the terms of the order.

13.16.3	Acceptance test:

The following tests shall be witnessed by the Purchaser through his representative at the firm’s works:

(i)	All the routine tests as mentioned above shall be performed on minimum 10% quantity of offered lot.

(ii)	Heat run test (Temperature rise test): Heat run test shall have to be conducted at suppliers cost on one transformer of each rating in any offered lot during the course of supplies. In case of transformers with tap changer, test shall be conducted on the lowest tap feeding corresponding losses at 750C.

To facilitate conduction of heat run test on any unit in any lot at any point of time during the supplies, the manufacturers will provide a thermometer pocket, which gets immersed in oil on the side of the transformer in all the transformers. This pocket shall also be used for connecting thermal sensing device to monitor the variations in temperature and whenever required to operate the protective devices. The Sensor pocket shall be of 12 mm diameter with blanking screwed cap, removable at site. The depth of the projecting stem of this pocket inside the transformer will be below oil level.  It shall not infringe with electrical clearances nor obstruct the un-tanking of the active part.

(iii)	Verification of active parts on one unit of each rating of ordered quantity along-with weighing of unit.

(iv) 	Unbalanced current test: The value of zero sequence current in the star winding shall not be more than 2% of the full load current.

(v)	Transformer shall be subjected to test for over fluxing of core, wherever required by the Company’s inspecting officer.

Further, the purchaser’s Inspector reserves the right to get the Spill Current Measurement Test and also the Pressure Test performed on any tank during their inspection.

(a)    	Air pressure test: The tank shall be fixed with a dummy cover with all fittings including bushings in position and be subjected to 0.8 Kg per cm sq. above atmosphere pressure for 30 minutes and the vacuum corresponding to (-) 0.7Kg per cm. Sq. for 30 minutes, permanent deflection for flat plate, after pressure has been released shall not exceed the values given below:

Length of plate				Deflection

Upto 750 mm				    5mm

751 to 1250 mm			    6 mm

1251 to 1750  mm			    8mm

(b)	Test for Spill Current in neutral: The test will comprise of measuring current between shorted secondary phases and neutral on applying impedance voltage at primary winding. The value should not exceed 2% of full load current.

13.17. 	Testing facilities

The bidder should have adequate testing facility for all routine and acceptance tests and also arrangement for measurement of losses, resistance, etc. details of which will be enumerated in the order.

13.18. 	Inspection

(A)	To ensure about the quality of transformers, the inspection shall be carried out by the Company’s representative or by third party at following two stages:

(i) 	Stage Inspection will be done when the raw material is received, and the assembly is in progress in the shop floor. After the main raw-materials i.e. core and coil materials and tanks are arranged and transformers are taken for production on shop floor and a few assembly have been completed, the firm shall intimate the O/o the CE(Engg),NRDA in this regard, so that an inspecting officer for carrying out such inspection could be deputed, as far as possible within fifteen days from the date of intimation. During the stage inspection, a few assembled cores shall be dismantled to ensure that the CRGO laminations of M4 Grade used are of good quality.

(ii) 	Final Inspection will be carried out at finished stage i.e. transformers are fully assembled and are ready for dispatch. As and when the transformers are ready for dispatch, an offer intimating about the readiness of transformers, for final inspection for carrying out tests as per relevant IS and as in Clause 16 above, shall be sent by the firm along with Routine Test Certificates. The Company shall normally arrange t13.he inspection at the earliest after receipt of offer for pre-delivery inspection.

(C)	In case of any defect/defective workmanship observed at any stage by the Inspecting Officer, the same shall be pointed out to the firm in writing for taking remedial measures. Further processing should only be done after clearance from the Inspecting Officer/ this office.

(D)	All tests and inspection shall be carried out at the place of manufacture unless otherwise specifically agreed upon by the manufacturer and purchaser at the time of purchase. The manufacture shall offer the Inspector representing the Purchaser all reasonable facilities, without charges, to satisfy him that the material is being supplied in accordance with this specification. This will include Stage Inspection during manufacturing stage as well as Active Part Inspection during Acceptance Tests.

(E) 	Random sample checking and testing of the transformer selected at random from the supplies made to the Area Stores shall be done for verification of technical details, design and losses as per approved G.T.P. drawings and technical specification of the order. In case of variations, the lot shall be rejected.

(F) 	The purchaser has all the rights to conduct the test including type tests, at his own cost by an independent agency whenever there is dispute regarding the quality of supply or interpretation of test results. In the event of failure of transformers in such tests, the expenses incurred in testing shall be to the supplier’s account as already mentioned above in case of random testing.

(G)	Test reports on the analysis of raw materials: The supplier shall furnish details of source(s) of raw-materials, test certificates and report on the analysis of electrolytic copper//Aluminium used for the winding and the steel used for core, insulation material and also other bought out items form Sub-suppliers.

13.19. 	Inspection & Testing of Transformer Oil

To ascertain the quality of the transformer oil, the original manufacturer’s tests report should be submitted at the time of inspection.  Also arrangements should be made for testing of transformer oil, after taking out the sample from the manufactured transformers and tested in the presence of purchaser’s representative.

13.20. 	Loading of Transformers

Transformer loading should be complied with IS:6600.

13.21	Drawing:-

13.21.1	A set of following drawings with all dimensions shall be submitted by the Bidder along with the offer:

- General Dimensional drawing.

- Core Assembly drawing.

- Internal Construction Drawing.

- Rating & Diagram Plate Drawing.

- HV/LV Bushings indicating measurement of creepage distances.

13.21.2	The drawings shall be of A-4 size only. The bidder should also supply along with his offer the pamphlets/literatures etc. for fittings/ accessories.

13.22	Finishings:

The exterior of the transformer and other ferrous fittings shall be thoroughly cleaned, scrubbed and given primary coat and two finishing coats of durable oil and weather resistant paint of enamel. The color of finishing coats shall be DARK GREEN confirming to IS: 5 of 1961 (colors for ready mixed paints) with conservator painted with white color. 3 stars(***) should be painted on white conservator with green paint clearly visible from ground to indicate that the transformer is a 3 star rating, besides the BEE labelling.

13.23	Guaranteed Technical Particulars:

The bidder should fill up all the details in GTP parameter list, the statement such as “as per drawings enclosed”, “as per NRDA/C.S.P.D.C.L.’s requirement” “as per IS” etc. shall be considered as details are not furnished and such offers shall liable for rejection.

- Street Lighting Automation

14.1.	Operational Features

i.   	Automatic Control and Remote Operation from Central Control Station to be provided with SCADA software.

ii.  	Remote operation through mobile phones at zonal level.

iii.  	Status indication of the operation at central location and to Maintenance Staff on their mobiles through SMS message.

iv.  	Remote  indication  of  faulty  feeders  at  central  station  and power  failure  message through SMS to zonal staff (alarm message).

v.  	Forced operation ON/OFF from central station and by mobiles through SMS for maintenance purpose.

vi.  	Event and alarm logging facility - can be customized for analysis of the fault duration and type of faults, etc.

vii.  	Security of operation by passwords.

viii.  	It should be possible to modify/change the authorized mobile phone no. of the zonal staff from Central SCADA by SMS

ix.  	The system shall communicate with the Energy Meter installed in the panel on RS 485 network  with  Modbus  protocol  and  collect  important  parameters  i.e.,  3  phases Voltages and Currents, KWH, Power Factor.

x.  	It should be possible to set a base current (each phase) from remote (by SMS). Any deviation  beyond  predefined percentage should be reported as an exception to the Zonal Staff Mobile phone  and Central SCADA by SMS with absolute value of the deviated parameter. The Voltage and Power  Factor limits shall be fixed as per the standards and should generate a message in case of an event.

xi.  	Continuous Load current measurement - for analysis of aging factor of the lamps and healthiness of the individual circuits.

xii.  	The system shall have an in-built Real Time Clock (RTC)

xiii.  	The system should generate an event message, in case it loses communication with the Energy  Meter   (for  whatsoever  reason)  and  generate  an  SMS  to  the  Mobile Maintenance Crew and Central SCADA

xiv.  	The communication of the SCADA shall be on a DSL/Leased line from the service provider’s SMS database.

xv. 	There will be a dedicated URL which should be accessible from Internet on a browser, which shall list all the messages exchanged through the 3 digit short code

xvi.  	Report generation – daily consumption report and Exception report for power failures. xvii.   Supervision, control & logging to be archived district and zone wise.

xviii.  	System can be de-fragmented in future for district level operation and control in addition to central control station.

14.2 	GSM based Street Light Automation System:

A) 	System Specification:

i)  	The Streetlight Control System with GSM Interface should have a Central control station SCADA with two way communication using SMS messages.

ii)  	Switching of 100 & 200 Amp continuous load consisting of Fluorescent Tube Lights, HPSV Lamps and Halogen Lamps

iii)  	The system should have a provision for remote and local operation with a three way selector switch.

| S. No. | Description |  | Qty. |
| --- | --- | --- | --- |
| 100/200 Amps GSM Switch Module Specification : |  |  |  |
| 1 |  | Logic Controller | 1 |
| 2 |  | Communication Module | 1 |
| 3 |  | RTC (Real Time Clock) Module | 1 |
| 4 |  | Communication Cable (RS232 / RS485 for Energy Meter) | 2 |
| 5 |  | GSM Modem | 1 |
| 6 |  | Suitable MCCB with Trip contact | 1 |
| 7 |  | Contactor 100A/200A | 1 |
| 8 |  | MCB, 2A, 220V AC, 2P | 1 |
| 9 |  | By-pass Switch of suitable rating | 1 |
| 10 |  | Enclosure (14 G, CRCA, (1050x600x250 mm) | 1 |
| 11 |  | Aux Relay | 1 |
| 12 |  | Isolation Transformer 415/200V, 200 VA | 1 |
| 13 |  | CTs (Cast Resin, Class 0.5, 100/5) - 3 nos. | 1 |
| 14 |  | Acrylic Sheet Shroud for bus bars | 1 |

B) 	Hardware Configuration

i)	4 pole MCCB suitable for Positive Isolation with a Trip Contact

ii)	3 Pole Contactor with Aux Contact and 220 V AC Coil

iii)	Controller with

CPU with DI-09, DO-07 RTC, 24 V DC Power Supply

1 x RS 485 Port (Modbus) for communication with Energy Meter

1 x RS 232 Port for communication with GSM Modem

iv)  	GSM Modem

v)  	Energy Meter (To be supplied by Discoms as free issue item for integration)

vi)  	Aux relay for interposing the command to contactor from Controller

vii)  	Class 0.5 or 1.0 (depending on the Meter Supplied by Discoms) Cast resin CTs for connecting the Energy meter

viii)  	Isolation Transformer (415 V AC / 200 V AC) for control supply

ix)  	2P MCB for control supply

x)  	The earth conductor GI of size 25 X 3 mm

(C)	 Panel Enclosure

i)	The panel shall be wall mounting cubicle type with four supports to accommodate 8 mm Bolts

ii)	Sheet steel thickness for complete enclosure to be 2 mm

iii)	Cable entry will be from bottom with a gland plate made of 3 mm sheet steel

iv)	25 x 10 mm Aluminum bus bars for each phase and neutral

v)	Bus bars shall be mounted on 130 mm long insulators

vi)	Control wiring shall be 1.5 sq. mm PVC insulated copper cable

vii)	CT wiring shall be 4 sq. mm PVC insulated copper cable

viii)	All control cables shall be ferruled at both ends as per drawing

ix)	Engraved Legend plates shall be provided for equipment designation

x)	‘Danger’ plate shall be provided on the LT compartment

xi)	Panel shall be painted in Siemens Grey Paint, shade no. RAL7032

xii)	A transparent Acrylic Sheet Shroud shall be provided in the LT compartment housing MCCB & Contactor.

xiii)	Two earthings to be provided to the GSM switch. The earth conductor of size 25 X 3 mm will be tapped from the nearest earth mat available.

(D) 	MCB

i)  	Should be ISI mark as per IS 8828:96 and IEC 898 with short circuit breaking capacity as 10 kA.

ii)  	Should be classified as per application. B Curve in this case iii)  Should be suitable for Isolation

iv)  	Should have positive contact indication

v)   	Let through energy should be of class 3

vi)  	Should have Low energy watt loss

vii)  	Should offer Protection degree of IP 20

viii)   	Should have grooved tunnel terminal

ix)  	Should have captive screws

x)  	Should have an endurance of 20, 000 Number of operations when energized

xi)  	Resistance to electrical shocks (or dielectric withstand) should be 2.5 KV

xii)  	Should have line load reversibility

(E)	MCCB

a)	 General

i)  	The circuit breakers shall comply with IEC60947.2 & IS 13947 part 2.

ii)  	The breaking capacity performance certificates shall be available for category A to the above   mentioned  standards.  The  test  shall  be  carried  out  under  the  breaking performance  during  the  ultimate  breaking  capacity  (Icu),  Ics  rating  =100%  Icu. Certificate for all the sequences (Sequence 1 mandatory) should be available.

iii)  	All circuit breakers shall have a rated operational voltage of 600V AC (50/60Hz).

iv) 	The rated insulation voltage shall be 600V and 660V at 50/60 Hz. for low breaking capacity and high breaking capacity MCCBs respectively.

v) 	There should be different levels of breaking capacities starting from 10kA upto 50kAfor flexibility in selection.

vi)  	The breaker shall be maintenance free and fully tropicalized. vii)  It all have 4 poles (switched neutral).

viii)  	Production site organization shall be certified to comply with ISO 9001 standard.

b)	 Construction

i)  	Operating mechanism shall be of the quick make quick break type, with the speed of operation  independent of the operator, and mechanically trip free from the operating handle so as to prevent the  contacts from being held closed against short-circuit and overload conditions. The operating mechanism shall be constructed to operate all poles in a multi-pole breaker simultaneously during opening, closing and tripped conditions.

ii)  	It shall not require any external power supply to operate the tripping mechanism.

iii)  	The  breakers  shall  be  operated  by  a  toggle  which  shall  clearly  indicate  the  three fundamental positions ON, OFF and TRIPPED.

iv)  	If required, the breaker will be equipped with rotary handles.

v)  	The breaking and extinction of the electrical arc shall be achieved by means of non- welding contacts and an arc chute surrounding these contacts.

c) 	Characteristics

i)  	The protection unit shall have Short circuit setting fixed at 10In +/- 20% as specified in IEC 947 and IS 13947 part2.

d)	 Operation

i)  	The electrical and mechanical endurance of the moulded-case circuit breakers should be as defined by IEC 947-2 standard.

ii)  	The moulded-case circuit breakers shall be equipped with a "push to trip" button in front to test operation and the opening of the poles.

e) Options

i)  Aarm contacts should be available for remote indication of circuit breaker trip condition. f) Installation

i)  The circuit breaker should provide the flexibility of terminating line and load from any direction. Manufacturers should test the circuit breaker for this condition and requisite test certificate should be available.

Phase barrier should be provided as a standard feature.

F) Contactor

i)  Should be conforming to IEC 60947-4-1, IS 13947 ii)  No. of Poles – 3

iii)  Insulation Voltage – 690 V

iv)  Impulse withstand voltage (Uimp) – 8 KV

v)  Insulation – Class ‘F’

vi)  Shock resistance 10/15 gn

vii)  Should pick-up @ 85 – 110% of control voltage viii)   Should drop @ 30-60% of control voltage

ix)  Operating time – 15 to 35 ms

x)  Suitable for switching HPSV Lamps (Very high in-rush considering the Capacitance in

HPSV)

xi)  The contactor should be designed and tested for at least 5, 000, 000 mechanical operations

& 1, 000,000 electrical operations

xii)  Should be possible to inspect the contact wear and easy contact replacement xiii)  Should have Mechanical ON/OFF indicator

xiv)  Should have provision for side mounted aux. Contacts

G) GSM Modem

i)  900/1800 Dual Band, GSM

ii)  GPRS Class B, Class 2 (28.8 Kbps down load, 14.4 Kbps up load)

iii)  Fully Type approved – R&TTE

iv)  CE Approved

v)  AT Command set (GSM 07.05 and 07.07)

vi)  Suitable for Data, SMS, Voice & Fax vii)   SIM Tool Kit Class 2

viii)  DTMF Function

ix)  Data circuit asynchronous, transparent, non transparent up to 14.4 Kbps x)   SMS – Text & PDU, Point to Point (MT/MO), Cell Broadcast

xi)  One user programmable I/O port for connecting external devices xii)  Input Voltage 5 – 30 V DC

xiii)  Current consumption: max. 450 mA (avg.), max. 2.5 A Peak, up to 35 mA in idle mode xiv)  SIM Holder

xv)  SMA Antenna (50 Ohm)

xvi)  Temperature -	Operation : -15 to +50 deg. C, Storage : -20 to 65 deg. C

H) Controller

i)  AC Power voltage range from 85 to 264 VAC.

ii)  DC Input voltage (positive or negative logic) operating at 24VDC with a range from

20.4VDC to 28.8VDC

iii)  Relay outputs capable of handling over 2 A of power.

iv)  TUV certified product line confirming to the following EMC standards

    - EN 61131-2, Amendment 1 (CI 7,8,10,11,12)

    - EN 50081-2 ; 1993

    - EN 50082-2 ; 1995

v)  confirming to UL standard of Class 1, division 2, Group A, B, C & D

vi)  Internal EEPROM for program backup vii)  1 x RS 485 Modbus Master Port

viii)  1 x RS 232 Port for Modem ix)   Insulation resistance.

x)  Between power and ground terminals: 10 M    minimum (500 VDC)

xi)  Between I/O and ground terminals: 10 M    minimum (500 VDC)

xii)  Noise resistance. AC power terminals: 1.5 kV, 50 ns to 1 µs. I/O terminals (coupling clamp): 1.5 kV, 50 ns to 1 µs

xiii)  Provision for Plug in EEPROM for programming and memory extension

xiv)  Programmable input filter. Input filter time can be changed during configuration. No filtering or filtering at 3 ms or 12 ms. I/O points are configured in groups

xv)  Storage Temperature of  -25 deg. C to + 70 degree C and operating temperature from 0 deg. C to + 55 degree C

xvi)  processor with a processing cycle time of 1 ms per 1000 instructions xvii)   IEC1131 compliant supporting ladder, Grafset, instruction list

xviii)  Powerful instruction set including arithmetic, logic, numeric, drum control, automation functional blocks, trigonometric & Boolean

xix)  Scanning: Normal (cyclical) or periodic (constant) (2 to 150 ms)

xx)  Execution time: 0.14 µs to 0.9 µs for a list instruction

xxi)  Inbuilt analogue adjustment points accessible from the front panel updated from each scan xxii)  Relative humidity handling from 30-95% without condensation

xxiii)  Should be able to generate AT Commands for Modem

xxiv)  Capable of embedding Real-time data into an SMS with Time Stamp xxv)   Programmable in Ladder and Grafset

xxvi)  Should be able to record the time of the last power loss

I) SCADA Software

i)  Shall be a reputed make with special functions required for the project

ii)  Should have unlimited tags (as the expected no. of tags are expected to touch 1 lac nos. or more

iii)  Should support standard databases such as SQL, Oracle, and Access etc. iv)  Should be OPC compliant

v)  Should have all the possibilities of protocols for future up gradation viz., IEC 60870-5-

101/104, DNP3.0 etc

vi)  Should have feature of creating Web Clients for future viewing vii)  Should have Crystal Reports integrated for report generation

14.3 DATA Transmission System :

The following options are to be considered:

i)  By SMS - Meter reading at predefined time periodically and same logged by the SCADA

software.

ii)  By direct polling by Central Station – the Central SCADA will call up each unit periodically and fetch details of metering from each location and update its records with date and time. In this case all controllers will have DATA enabled SIM from GSM service provider.

iii)  By continuous Connection with the field control units – this option enables the central station to be always in touch with all field controllers and can keep on logging at very frequent intervals.   In   this   case   all   controllers   will   have   GSM   modems   with   GPRS/EDGE communication capability provided by the GSM service provider.

14.4 Location of GSM switches:

The Location of GSM switches have been categorized into the following three categories:

a)  Category I: Location of GSM switch within the sub station building

i)  This category is assumed / estimated to have a population of 60% of the installations

ii)  The GSM switch would be installed on wall by using Anchor Fasteners.

b)  Category II: Location of GSM switch in the outdoor kiosks

i)  This category is assumed / estimated to have a population of 30-35% of the installations

ii)  The GSM switch would be installed within the existing out door kiosk on the existing PCC poles.

iii)  It is envisaged that at some locations it may not be possible to install the GSM switch  within the existing fenced outdoor kiosk, in which case the GSM would be installed near to the kiosk or a separate MS Angle frame fabricated from 50 X 50 X 6 mm angle and grouted in ground and the entire area would be suitably fenced.

c)  Category III: Location of GSM switch in congested areas and Flood light Masts i)  This category is assumed / estimated to have a population of 10-15% of the

installations

ii)  The flood light masts may be connected to the street light circuit. iii)  The GSM switch would be installed in the indoor substations

d)  High Mast : Falling in proximity of any of the above 3 categories

i)  The flood-light masts may be connected to the GSM Switches on existing circuits falling in any of the above categories

ii)  Necessary modification need to  be carried out to by-pass the existing high- mast control panel

14.5 Supply and cabling:

1. The LV supply to the GSM switch will have Incoming cable size of 4 Core 50 sqmm( for 100 amp switch) and 4core 95 sqmm cable (for 200 amp switch) XLPE cable and subsequent section of the  street light mains shall be done through	4 Core 25 sqmm XLPE cable.

2. The connections from Junction/fuse box to the Luminaries shall be done with 2.5

Sqmm multistrand copper conductors.

14.6 Provisions of IER : 1956

Bidder shall comply with provisions of Indian Electricity Rules 1956 as amended/updated.

14.7 Standards

Relevant IS shall be followed in all cases. For any aspect for which IS is not available

International Standards such as IEC/BS shall be followed.

15.	11 KV RING MAIN UNIT

Scope of work : Design, Engineering, Manufacturing, assembly,  inspection and testing before  despatch,  packing  &  forwarding  and  delivery  at  site/stores  of  outdoor  type compact 11KV Oil Ring  Main  Units with Load break Isolators for 11 KV Incoming & Out  going  cables  and  HT HRC fuse unit for  Distribution  Transformer  with  future  provisions  for motorization  and  necessary  take  off  terminal  units  for  future  SCADA  automations, other accessories and auxiliaries equipments and mandatory spares,  described herein and   required for their satisfactory operation in various   locations of the  Naya Raipur,  in  combinations  of  2 LBS + 1 HT HRC fuse BOTH SIDE EXTENSIBLE and all these units are shielded in a outdoor metal body with a dielectric media  of Oil with provision of additional load break switches and HT HRC fuses extensible at both side:-

Provision   of   all   the   RMU   with   necessary   take   off   terminal   units   for   future   SCADA automations.

15.1	The  objective  of  the  RMUs  is  for  extremely  small  construction  width,  Compact, maintenance free, independent of climate, easy installation, operational reliability, Safe and easy to operate,  minimum construction cost, minimum site work and minimum space	requirement.

15.2	The  RMUs  shall  conform  in  all  respects  to  high  standards  of  Engineering  design, workmanship  and  latest  revisions  of  relevant  standards  at  the  time  of  offer  and purchaser shall have the right to reject any material which in his judgment is not in full accordance therewith.

15.3	The insulating medium for load break isolators, HT HRC fuse unit, Earth switch, 11 KV Buses and other associated equipments should be oil confirming to relevant IS/IEC.

15.4	The  complete	RMU  must  be  fully  Type  Tested  including  for  Internal  Arc  Fault withstand for 20KA / 0.1 Seconds. as per latest Standard IEC 62271-100/200.

15.2	STANDARDS :

Unless  otherwise  specified  elsewhere  in  this  Specification,  the  RMU,  Switchboard (Switchgear),  Load  break  isolators,  Instrument  Transformers  and  other  associated accessories	shall  conform  to  the  latest  revisions  and  amendments  thereof  of  the following standards.

| IEC 60 298/ IEC 62271-200/IS 12729:1988 | General requirement for Metal Enclosed Switchgear |
| --- | --- |
| IEC62271-102/ IS 9921 | Alternating current Dis-connector’s (Load break isolators) and Earthing switch |
| IEC 62271-100/ IEC 62271-200 | Specification for alternating current circuit breakers. |
| IEC 60044-1/IEC 60185/IS 2705:1992 | Current Transformer |
| IEC 62271-103 | High voltage switches |
| IEC 60273/IS :2099 | Dimension of Indoor & Outdoor post insulators with voltage > 1000 Volts |
| IEC 60529/IS 13947(Part-1) | Degree of protection provided by enclosures for low voltage switchgear and control gear |
| IEC 60255 | Electrical Relays |
| IEC 60265 | Specification for high-voltage switches |

The following parts of RMU shall be type tested for Degree of protection:-

IP 67  -	tank with high voltage components. IP 2X   -	front covers of the mechanism.

IP 3X  -  cable connection covers. IP 54   -  outdoor enclosure/kiosk.

Equipment meeting with the requirements of any other authoritative standards, which ensures  equal  or  better  quality  than  the  standard  mentioned  above  shall  also  be acceptable. If  the  equipments,  offered  by  the  Bidder  conform  to  other  standards, salient points of difference between the standards adopted and the specific standards shall be clearly brought out in relevant schedule. In case of any difference between provisions  of   these  standards  and  provisions  of  this  specification,  the  provisions contained  in  this  specification  shall  prevail.  One  Hard  copy  of  such  standards  with authentic English Translations shall be furnished along with the offer.

15.3.	SERVICE CONDITIONS:

All  out door  Equipment /  material  to  be  supplied  against this  specification  shall  be suitable  for  satisfactory  continuous  operation  under  tropical  conditions  as  specified below:-

(i)	 Peak Outdoor temperature 		: 50 0 C Minimum (50 0 C+40 0 C)

(ii)	Maximum oil temperature		: (50 0 C+35 0 C)

: 850C under max. temperature & max load    						   condition attainable.

(iii)	Maximum relative humidity		: 95% (sometime approaches saturation

point).

(iv)	Minimum relative humidity		: 10%

(v)	Average No. of thunderstorm		: 40 days

days per annum.

(vi)	Average number of rainy days   	: 90 days

(vii)	Number of months of tropical		: 3 months

monsoon conditions.

(viii)	Average annual rainfall		: 125 cm.

(ix)	Wing pressure			: 100 Kg/m2

(x)	Altitudes not exceeding		: 1000 meters.

15.4	TECHNICAL PARAMETERS OF RMU: I.	11KV Bus Bar

Type of material	: Copper

Current Carrying Capacity 	: 400 Amps. Short time rating current for 3 secs.	: 13.1 kA

Insulation of bus bar	: Oil

Bus bar connections	: Anti-oxide grease

II.	Parameters for  Switch Gear of DT  and  load break isolators

Type 	: Metal enclosed

No of Phases 	: 3

No. of poles	: 3

Rated voltage 	:12 KV

Operating voltage 	:11 KV(+10% to –20%) Rated lightning impulse withstand voltage 	:75 KV

Rated power frequency withstand voltage 	:28 KV

Insulating medium	: Oil

|  | Rated short time current Rated short time Rated peak withstand current | :13.1 KA. :3s :35 KA. |
| --- | --- | --- |
|  | Rated current (Bus): Rated current Load Break Isolator: Rated current (HRC fuse) Rated frequency | :400 A :400 A :200 A : 50 Hz |
|  | Number of mechanical/Remote operations for earthing & Ring switches | : 1000 Nos. |
| III. | PRINCIPAL FEATURES: |  |

| S. No | DESCRIPTION | DT breaker |  |
| --- | --- | --- | --- |
| 1 | Circuit label | Yes |  |
| 2 | Mimic diagram | Yes |  |
| 3 | Supply voltage indication | Yes |  |
| 4 | Current Transformer | Yes |  |
| 6 | Anti–Reflexing Mechanism | Yes |  |
| 7 | Interlock to defeat the operation of the line side earthing when the line side isolator is ON. | Yes |  |
| 8 | Interlock to defeat the operation of the earthing when the breaker is in service position and is ON. | Yes |  |
| 9 | Local /Remote Switch | Yes |  |
| 10 | ON/OFF indication | Yes |  |
| 11 | Spring Charge indication / Spring assisted mechanism. | Yes |  |
| 12 | Fault Tripping indication | Yes |  |
| 13 | Bus bar end caps |  | Yes |
| 14 | Whether the SF6 gas pressure gauge indicator and filling arrangement. |  | Yes |
| 15 | Whether the spring assisted mechanism with operating handle for ON/OFF. |  | Yes |
| 16 | Whether the earth positions with arrangement for padlocking in each position and independent manual operation with mechanically operated indicator are provided |  | Yes |
| 17 | RMUs are provided with necessary take off terminals for future SCADA automation. |  | Yes |

IV.1	Load break switch(Isolators) :

Type : load breaking  and fault making.

Rated current		:	400 A

Fault making capacity (KA peak min.)	:	31.5 KA

IV.2	Earthing switch for 11 KV Line side Isolation and DT :

Rated short time current	:13.1 KA.

Rated short time	:3s

Rated peak withstand current	:35 KA

Interlocking facility			: 1) Between 11 KV Line side isolator ‘ON”& 					              Earthing.

2) Between 11 KV DT side HT 				                        HRC on close condition & Earthing.

15.5.	GENERAL CONSTRUCTION FEATURE FOR RING MAIN UNIT:

The compact RMU shall be designed to operate at the rated voltage of 12 KV.  It shall include,  within  the  same  metal  enclosure,  earthing  switches  for  each  Load  Break Switch  and  HT HRC fuse earthing  each  of  the  devices.  Suitable  fool-proof interlocks shall be provided to these earthing  switches to prevent its inadvertent or accidental closing when the circuit is live and the concerned Load Break Switch/Circuit Breaker is in closed position.  The degree of protection required against  environment shall be not less than IPX4 of IS 12063. The Compact RMU shall have atleast an IP54  Protection Index as per IS 12063 against dust and splashing of water.  The active parts of the switchgear shall be maintenance free and the Compact RMU shall be of low-maintenance type.

15.5.1	The  Ring  Main  Unit  shall  be  installed  at  11  KV  junction  points  to  have  continuous supply by isolating faulty sections. The RMU shall be both side extensible and consists of the combinations of load  break switches and HT HRC fuse for a nominal voltage of 12 KV using oil as insulating and arc quenching medium.

15.5.2	The RMU and combination shall be outdoor metal enclosed type. The RMU metal parts shall be of high thickness high tensile steel which must be grit/short blasted, thermally sprayed with Zinc alloy, phosphate and subsequently painted with polyurethane based powder paint, the overall paint layer thickness shall be not less than 80 microns.

15.5.3	Relevant IE rules for clearances, safety and operation inside the enclosure shall  be  applicable.  The  enclosure  shall  be	free  from  pollution,  humidity,  dust, vermin   etc.   IP-54   and   type   tested   for   accelerated   aging   &   weather   proof   at EREDA/CPRI/any other testing house meeting PQR.

15.5.4	All high voltage live parts except for the cable connections shall be insulated with Oil.  The  Oil  enclosures  shall  be  made  of robotically/laser / TIG/ MIG  welded stainless steel/ hermetically sealed metalized cast resin tank without use of sealant, gaskets,  ‘O’  rings, etc. and shall be type tested for IP-67 Degree of protection.

15.5.5	The cubicle shall be touch proof metallic encapsulation with a electro galvanized sheet steel of high  thickness and provided with a pressure relief arrangement away from operator.

15.5.6	RMU  should  be  suitable  for  motorization  in  future  for  remote  operation through SCADA.

15.5.7	Any accidental over pressure inside the sealed chamber shall be limited by the opening of a  pressure-limiting device in the rear/top part of the enclosure. Oil will be release to  the  rear  of  the  switchboard  away  from  the  operator  to  ensure  safety  of  the operating personnel and all the  manual operations will be carried out on the front of the switchboard.

15.5.8	The enclosure for switchgear and metallic RMU housing shall have a design such that in  the  event  of  an  internal  arc  fault,  the  operator  shall  be  safe.  This  should  be  in accordance  with  IEC  298  &  Standard  IEC  62271-100/200  and  relevant  TYPE  TEST certificates shall be submitted.

15.5.9		The  Entire  units  of  RMU  shall  be  in  a  single  compact  metal  clad  weather  proof enclosure,  outdoor type suitable for all weather conditions. The switchgear and bus bar  shall  all  be  filled  with  oil  IEC/IS  Standards  relative  pressure  ensure the insulation and breaking functions. The enclosure must be sealed for life and shall meet the  “sealed pressure system” criterion in accordance with the IEC 298 & 62271-100/200 standard.

15.5.10	Suitable temperature rise test on the RMU with enclosure shall be carried out as per relevant IEC/IS.

15.5.11	Each  switchboard  shall  be  identified  by  an  appropriately  sized  label,  which  clearly indicates the functional units and their electrical characteristics.

15.5.12	The switchgear and switchboard shall be designed so that the position of the different devices is  visible  to the operator on the front of the switchboard and operations are visible as well.

15.5.13	The entire system shall be totally encapsulated. There shall be no access to exposed conductors.  In  accordance  with  the  standards  in  effect,  the  switchboards  shall  be designed so as to prevent  access  to all live parts during operation without the use of tools.

15.5.14	The entire 11 KV RMU  shall be insulated by Oil suitable for operating  voltage up to 12 KV respectively.

15.5.15	The  tank  shall  be  made  of  suitable  stainless  steel/  cast  resin  tank  of  adequate thickness  and  shall  be  able  to  withstand  any  accidental  internal  over  pressure  of atleast 3 bars.

15.5.16	The Compact RMU shall be suitable for mounting on its connecting cable trench. A suitably  sized   nameplate  clearly  indicating  its  functional  units  and  their  electrical characteristics shall identify  each  unit. The positions of the different devices shall be clearly visible to the operator on the front  of the compact RMU and the operations shall be clearly visible. The compact RMUs shall be such that access to live parts shall not be possible without the use of tools.

15.5.17	The design shall incorporate such features to prevent any accidental opening of the earth switch when it is in closed position. Similarly accidental closing of Load Break Switch shall  be  prevented when the same is in open position from the release  of  any  latch  or  spring  in  tension   due  to  vibrations  caused  externally  or internally and shall prevent accidents.

FORMATION OF  COMPACT  RMU:

15.5.18	The compact RMU shall be of single busbar outdoor, tropicalized in accordance with the relevant clauses mentioned in these specifications. An earth fault passage indicator using a core balance Current Transformer shall be provided for the Incomers to assist in identifying the faulty cable section in order to isolate the same.

15.5.19	The Incomers panel shall comprise of, but not limited to the following:

The earth fault passage indicators (The indicator flag of the relay shall be visible till 	such time the relay is reset manually). These shall not require any external Power Supply and must be suitable for unattended places.

15.5.20	The  transformer  loop  circuit  control  panels  shall  consist  of  but  not  limited  to  the following:

A HT HRC fuse rated 50 Amps or higher, with a rated making capacity under fault conditions with short circuit levels of 13.1 KA.

15.6	Oil

The transformer shall be supplied complete with first filling of oil and the same shall comply with IS: 335-1983 with latest version thereof with ageing characteristics specified. These characteristics are as per IS. Type tests certificate of oil being used shall be produced at the time of inspection.

            - The units shall be supplied with the complete insulating medium. The recommended insulating medium for switch chambers is oil. However, equipment with any other approved insulating medium offered and supported with full technical particulars could be considered.

            - Relevant gauge indicators and Sample testing facilities should be provided if the medium is oil.

            - Design and application of the insulating medium in the unit shall be in strict compliance to the relevant standard specification specified.

15.7	RMU OUTDOOR METAL CLAD:-

The  RMU  enclosure  must  be  a  metallic;  it  follows  an  industrialized  process  of manufacturing. The RMU shall be of single bus bar Oil insulated outdoor, tropicalised and metal  enclosed type. The RMU metal parts shall be made of high thickness high tensile steel which must be  grit/short blasted, thermally sprayed with Zinc alloy, phosphate and subsequently painted with polyurethane based powder paint, the overall paint layer thickness shall be not less than 80 microns.

TAKE  OFF TERMINAL UNITS FOR FUTURE AUTOMATION :

The RMU should be provided with necessary take off terminal units for future	SCADA automations.  Both  the  load  break  switches  and  the  tee  off  circuit  breaker  shall  be suitable for motorization in future.

15.8.	ISOLATORS (LOAD BREAK TYPE) :

The load break isolators for Incoming and Outgoing supply must be provided and the load break  isolators are fully insulated by Oil. The load break isolators  shall  consist  of  400  Amp  fault  making/load  breaking  spring  assisted  ring switches, each with integral fault making earth switches. The switch shall be naturally interlocked  to  prevent the  main  and  earth  switch  being  switched ‘ON’  at the  same time. The selection of the main and earth switch is made by a lever on  the fascia, which is allowed to move only if the main or earth switch is in the off position. The load  break isolators should have the facility for future remote operation. Each load break switch shall be  of the triple pole, simultaneously operated, non automatic type with quick break contacts and with integral earthing arrangement.

The	earthing  switch  shall  also  be  designed  for  rated  fault  making of 50KA for operator’s safety reasons.

15.9.	SCADA CONNECTIVITY:

Provision  shall  be  made  in  all  the  RMUs  with  necessary  take  off  terminal  units  for future automations / SCADA connectivity.

15.10	HT HRC Fuse  :

(i) Fuse links shall be provided on a removable carriage and the opening of the fuse chamber access cover shall dis-connect the carriage in order to provide double disconnection.

(ii) Latching arrangements of fuse carriage, after partly lifting for full access of fuses, shall be provided.

(iii) The fuses shall be in accordance to Schedule of Technical Requirements.

15.11.	BUSHINGS :

The units are fitted with the standardized bushings that comply with IEC standards.

All	the bushings are the same height from the base and are protected by a cable cover. All the   bushings  shall  be  Partial  Discharge  free  &  preferably  Laser  welded with the SS	container in case of stain less steel  tank type RMU.

15.12 CABLE BOXES :

All the cable boxes shall be air insulated suitable for dry type cable terminations. The cable boxes at each of the two ring switches shall be suitable for accepting HV cables of sizes 3c x 240 / 3c x 185 sq.mm and circuit breaker cable be suitable up to 3c x 50 sq.mm.

Necessary Right angle Boot should be supplied to the cable terminations. The type of the Right angle Boot should be cold applied insulating Boot.

A non Ferro- magnetic cable clamp arrangement for 3 core XLPE cables must be provided for all cables terminated on the RMU. Glands in the base plate of the RMU shall be provided for proper Cable termination.

15.13.	FAULT PASSAGE INDICATORS (FPI):

This  shall be integral part of the RMU and shall be provided to assist in identifying the faulty cable section in order to isolate the same. The Fault Passage Indicators (FPI) shall have automatic rest facility and shall be suitable for trouble free operation. The indicator flag of the relay shall be visible till such time the relay is reset. LED indicating bulb should be provided for better visibility particularly in day time The relay should not require any external power supply

15.14.	CABLE TESTING FACILITY :

It shall be possible to test the cable without opening  the cable boxes or ‘where there is no provision  for testing the cable without opening the door or cover’, opening of door or cover should not be  possible unless the earthing switch is closed as per IEC 298  clause  5.102.4.  The  cable  testing  should  be  possible  without  dismounting  the cable plugs but the after opening the cable covers.

15.15.	VOLTAGE INDICATOR LAMPS AND PHASE COMPARATORS :

The RMU shall be equipped with a voltage indication to indicate whether or not there is  voltage  on  the  cable.  There  should  be  a  facility  to  check  the  synchronization  of phases with the use of external device. It shall be possible for the each of the function of the RMU to be equipped with a permanent voltage indication as per IEC 601958 to indicate whether or not there is voltage on the cables. The  indicating lamp shall be LED type for  better visibility during day light.

15.16.	EXPANDABILITY :

Each combination of RMU shall have the provision for future extension on both sides by  load  break  isolators  /  HT HRC fuse,  with 	a  suitable  trunking  chamber  and accessories and necessary Bus Bar. Extensible isolator(s) and circuit breaker(s) shall be individually  housed in a separate Oil epoxy enclosures. Even in case of extensible HRC, the HRC fuse should be capable of necessary   short circuit operations as per IEC,  and  the HT HRC fuse should have a rated current carrying capacity of 200 A.

15.17.	BUS COUPLER/ BUS BAR SECTIONALISER WITH LOAD BREAK SWITCH

The load break switch of the Bus bar Sectionaliser shall be rated for 12 KV, 400A,

13.1 KA  for  3  secs.  The  LBS  should  be  housed  in  a  oil  Insulated stainless steel enclosure conforming to IP-67 Degrees of protection and shall be with motorized  mechanism. The sectionaliser shall be provided with all the necessary electrical and mechanical interlocks required for proper functioning with the Incomers.

15.18.	PADLOCKING FACILITIES

Provision shall be made for padlocking the load break switch /HRC fuse and the earthing  switches in either open or closed position with lock & master key. The circuit breakers and earthing switches can be locked in the open or closed position by 1 to 3 padlocks 6 to 8 mm in diameter.

15.19.	WIRING & TERMINALS:

The wiring should be of high standard and should be able to withstand the tropical weather conditions. The wiring cable must be standard single-core non-sheathed, Core marking  (ferrules),   stripped  with  non-notching  tools  and  fitted  with  end  sleeves, marked in accordance with the circuit diagram with printed adhesive marking strips. All wiring  shall  be  provided  with  single  core  multi-strand  copper  conductor  wires  with P.V.C  insulation  and  shall  be  flame  retardant  low  smoke  type.  The  wiring  shall  be carried out using multi-strand copper conductor super flexible PVC insulated  wires of

650/1100V  Grade  for AC  Power,  DC  Control  and  CT circuits.  Suitable  colored  wires shall be used for phase identification and interlocking type ferrules shall be provided at both ends of the wires for wire identification. Terminal should be suitably protected to eliminate sulphating.  Connections and terminal should be able to withstand vibrations.

The  terminal  blocks  should  be  stud  type  for  controls  and  disconnecting  link  type

terminals for CT leads with suitable spring washer and lock nuts.

Flexible wires should be used for wiring of devices on moving parts such as swinging Panels (Switch  Gear) or panel doors. Panel wiring shall be securely supported, neatly arranged readily accessible and connected to equipment terminals, terminal blocks and wiring gutters. The cables should be uniformly  bunched and tied by means of PVC belts and carried in a PVC carrying trough.

The position of PVC carrying trough and wires should not give any hindrance for fixing or removing  relay casing, switches etc., Wire termination shall be made with solder less crimping type of tinned  copper lugs. Core identification plastic ferrules marked to correspond  with  panel  wiring  diagram  shall  be  fitted  with  both  ends  of  each  wire. Ferrules shall fit tightly on the wire when disconnected. The  wire number shown on the wiring shall be in accordance with the IS.375.

All wires directly connected to trip circuits of breaker or devices shall be distinguished by addition of a red color unlettered ferrule.

Inter-connections to adjacent Panels (Switch Gear) shall be brought out to a separate set of Terminal blocks located near the slots or holes to be provided at the top portion of the panel.	Arrangements shall  be made for easy connections to adjacent Panels (Switch Gear) at site and wires for this purpose  shall  be provided and bunched inside the panel. The bus wire shall run at the top of the panel. Terminal block with isolating links should be provided for bus wire. At least 10% of total terminals shall be provided as spare for further connections. Wiring shall be done for all the contacts available in the  relay  and  other  equipment  and  brought  out  to  the  terminal  blocks  for  spare contacts. Colour code for wiring is preferable in the following colours.

Voltage supply 	:  Red, Yellow, Blue for phase and Black for

Neutral

CT circuits	:  Similar to the above

DC circuits	:  Grey for both positive and negative

250V AC circuits	:	Black for both phase and neutral

Earthing 	:	Green

The wiring shall be in accordance to the wiring diagram for proper functioning of the connected equipment. Terminal blocks shall not be less than 650V grade and shall be piece-molded type with insulation barriers.

The  terminal  shall  hold  the  wires  in  the  tight  position  by  bolts  and  nuts  with  lock washers. The  terminal blocks shall be arranged in vertical 	formation at an inclined angle with sufficient space between terminal blocks for easy wiring.

The  terminals  are  to  be  marked  with  the  terminal  number  in  accordance  with  the circuit  diagram  and  terminal  diagram.  The  terminals  should  not  have  any  function designation and are of the tension spring and plug-in type.

15.20.	EARTHING :

EARTHING 	OF 	ISOLATORS 	AND 	DISTRIBUTION 	TRANSFORMER HT HRC Fuse (EARTH SWITCH) :

Necessary   arrangements   shall   be   made   at   Load   break   isolators   /   Distribution Transformer Fuse  for selecting Earth position. Mechanical interlocking systems shall prevent the RMU function  from being operated from the ‘ON’ to ‘Earth On’ position without going through the ‘OFF’ position.

The   RMU   outdoor   metal   clad,   Switch   Gear,   Load   break   isolators,   Distribution Transformer ,LT pillar box, & steel structure  etc., shall be equipped with an earth bus securely fixed along the base of the RMU.

15.21.  ACCESSORIES & SPARES:

The  following  spares  and  accessories  shall  be  supplied  along  with  the  main equipments at free of cost:-

1.	Charging lever for operating load break isolators & circuit breaker of each RMU

2.	Kit for identifying oil leakage – 1 numbers

3.	All pressure gauges indications – 1 numbers

4.	Necessary oil filling plant with  adopter and tools etc for filling oil at

Site --1 Nos

5.	6.	Any  other  spares  &  Tools,  which  are  all  essentially  required  at  the  time  of emergency and routine maintenance.

The following accessories shall be supplied with each compact RMU at free of cost:

1.	Pad locks for all doors with one set (3 Nos.) Master keys

2.	Earth bus formed out of 30X5 mm tinned Copper flat.

3.	Wire  guard  protective  mesh  on  the  front  doors  and  back  for  prevention  of pasting of papers etc.

4.	Base channel with foundation bolts

5.	Live part shrouds, danger plates, caution boards, name plates, rating plates etc. as per requirements

6.	All other components, even though not specifically mentioned, but required for the safe operation of the unit.

15.22.	TESTING OF EQUIPMENT & ACCESSORIES:

15.22.1   INSPECTION & TESTIMG :

The inspection may be carried out by the NRDA at any stage of manufacture.	The supplier  shall  grant free  access to  NRDA’s representative  at any  reasonable  time when the work is in progress..

The supplier shall keep the NRDA informed in advance, about the manufacturing programme so that arrangement can be made for inspection. The NRDA reserves the right to insist for witnessing  the acceptance/routine testing of the bought out items..

No material shall be dispatched from its point of manufacture unless the material has been  satisfactorily  inspected and tested / unless the same is waived by the NRDA in writing.

15.22.2   ACCEPTANCE AND ROUTINE TESTS :

All acceptance and routine tests as stipulated in the latest relevant IS/IEC shall be carried out by the supplier at his works in the presence of Nigam’s representative.The supplier shall give at least 15  days advance intimation to the DISCOM to enable them to depute their representative for witnessing  the tests. The cost towards these tests and other expenses shall be borne by the supplier.

15.22.4   TYPE TEST

The Tenderers should, along with the tender documents, submit copies of all Type test certificate of  their make in full shape as confirming to relevant ISS/IEC of latest issue obtained from a   laboratory/  testing house as detailed in Pre Qualifying Requirement (PQR) attached with.

The above type test certificates should accompany the drawings for the materials duly signed and  certified by the institution who has issued the type test certificate. The following type test certificate shall be provided:

| S. No. | Name of Type Test |
| --- | --- |
| 01. | Short time current withstand test and peak current withstand test. |
| 02. | Lightning Impulse voltage with-stand test |
| 03. | Temperature rise test |
| 04 | Short Circuit current making and breaking tests CB Isolator |
| 05. | Power frequency voltage withstand test (dry/wet) |
| 06 | Capacitive current switching test confirming to IEC |
| 07. | Mechanical Endurance Test confirming to IEC / |
| 08 | Measurement of the resistance of the main circuit. |
| 09 | Checking of degree of protection |
| 10 | Switch, circuit breaker, earthing switch making Capacity  CB  Earth Switch |
| 11 | Switch, circuit breaker, earthing switch breaking Capacity  CB |
| 12 | Internal Arc Withstand |
| 13 | Partial Discharge test on Complete RMU |
| 14 | Other type & routine tests insists by IEC for RMU |

15.23   PERFORMANCE GUARANTEE

The performance Guarantee period shall be 2 (Two) years from the date of receipt of equipment along with its all accessories.

15.24  DOCUMENTATION

15.24.1   DRAWINGS

The  tenderer  shall  submit  along  with  his  tender  dimensional  general  arrangement drawings  of   the  equipments,  illustrative  and  descriptive  literature  in  triplicate  for various items in the  RMUs which are all essentially required for future automation.

i)	Schematic diagram of the RMU panel ii)	Instruction manuals

iii)	Catalogues  of  spares  recommended  with  drawing  to  indicate  each  items  of spares

iv) 	List of spares and special tools recommended by the supplier. v)	Copies of Type Test Certificates as per latest IS/IEC.

vi) 	Drawings of equipments, relays, control wiring circuit, etc. vii)	Foundation drawings of RMU.

viii) 	Dimensional drawings of each material used for item Vii.

ix) 	Actual single line diagram of RMU/RMUs with or without Extra combination shall be  made  displayed  on  the  front  portion  of  the  RMU  so  as  to  carry  out  the operations easily.

The following should be supplied to each consignee circle along with the initial supply of the equipments ordered.

5 copies of printed and bound volumes of operation, maintenance and erection manuals in  English along with the	copies of approved drawings and type test reports etc.

3 sets of  the  manuals  as  above  shall  be  supplied  to  the  Superintending

Engineer(MM), JVVNL, Jaipur.	A  soft  copy  of  the  all  Technical  and  Drawing furnished in a CD.

All  drawings  shall  conform  to  relevant  International  Standards  Organization  (ISO) Specification. All drawings shall be in ink and suitable for microfilming.

15.24.1.1 	All drawings submitted by the Supplier including those submitted at the time of bid shall  be  in   sufficient  detail  to  indicate  the  type,  size,  arrangement,  dimensions, material description, Bill of Materials, weight of each component, break-up for packing and  shipment,  required  fixing  arrangement,  the  required  dimensions  for  installation and any other information specifically requested in the Specification.

15.24.1.2 	Each drawing submitted by the Supplier shall be clearly marked with the name of the Purchaser, the  unit  designation, the Specification title, the Specification number and the name of the Project. All  titles, noting, markings and in writings on the drawing shall be in English. All the dimensions should be to the scale and in metric units.

15.24.1.3 	The drawings submitted by the Supplier shall be reviewed by the Purchaser as far as practicable within  15 days and shall be modified by the Supplier if any modifications and / or corrections are required by the Purchaser in compliance with the Specification. The Supplier shall incorporate such modifications  and or corrections and submit the final drawings for approval. Any delays arising out of failure by the  Supplier to rectify the drawings in good time shall not alter the completion date.

15.24.1.4 	The drawings submitted for approval to the Purchaser shall be in quadruplicate. One print  of  such  drawings  shall  be  returned  to  the  Supplier  by  the  Purchaser  marked “approved  /  approved  with  corrections”.	The  Supplier  shall  thereupon  furnish  the Purchaser  additional  print  as  stipulated  in  Technical  Specification  along  with  one reproducible in original of the drawings after incorporating all corrections.

15.24.1.5 	Further work by the Supplier shall be strictly in accordance with these drawings and no deviation  shall  be  permitted  without  the  written  approval  of  the  Purchaser,  if  so required.

15.24.1.6 	All manufacturing and fabrication work in connection with the equipment / material prior to the  approval of the drawings shall be at the Supplier’s risk. The Supplier may make any changes in the design, which are necessary to make the equipment conform to the provisions and intent of the Contract and such changes will again be subject to approval by the Purchaser. Approval of Supplier’s  drawing or work by the Purchaser shall  not  relieve  the  Supplier  of  any  of  his  responsibilities  and  liabilities  under  the Contract.

15.24.1.7 	All rights of the design / drawing shall be strictly reserved with the Purchaser only and any designs / drawings / data sheets submitted by the supplier from time to time shall become the property of the  Purchaser. Under no circumstances, the Supplier shall be allowed to use / offer above designs /  drawings / data sheets to any other authority without  prior  written  permission  of  the  Purchaser.  Any  deviation  to  above  is  not acceptable and may be a cause of rejection of the bid.

15.24.2   NAME PLATE:

Each RMU and its associated equipments shall be provided with a nameplate legible and indelibly marked with at least the following information.

(a)	Name of manufacturer

(b)	Type, design and serial number

(c)	Rated voltage and current

(d)	Rated frequency

(e)	Rated symmetrical breaking capacity

(f)	Rated making capacity

(g)	Rated short time current and its duration

(h)	Purchase Order number and date

(i)	Month and Year of supply & Expiry of Guarantee period

(j)	Rated lighting impulse withstand voltage

(k) 	D.C. component of current.

(l)	Feeder name(Incoming and Out going),DTs Structure name,11000Volts

Dangers etc.

NOTE:	i) The word rated need not appear on the name plate. Recognized abbreviations may be used to express the above particulars.

ii)Whether the circuit breaker is fitted with closing/tripping  devices necessitating an auxiliary supply shall be stated either on the circuit breaker name plate or any other acceptable position.

15.25.	TRAINING:

The supplier shall give rigorous training to at least 2 NRDA Engineers & staff at the site  for  3  days  in  attending  trouble  shooting  and  maintenance.  The  cost  towards transport, food and other expenses shall be borne by the supplier.