## COST ABSTRACT
COST ABSTRACT FOR THE "CONSTRUCTION OF PANCHAYAT AND RURAL DEVELOPMENT DEPARTMENT BUILDING AT SECTOR-19 IN NAYA RAIPUR"
SL. NO. | DESCRIPTION OF ITEMS | AMOUNT IN INR
|  | IN FIGURES | IN WORDS
A | CIVIL WORK | 0
B | ROAD WORK | 0
C | ELECTRICAL WORK | 0
D | HVAC WORK | 0
E | PLUMBING WORK | 0
F | FIRE FIGHTING WORK | 0
| TOTAL AMOUNT IN INR (IN FIGURES) | 0
TOTAL AMOUNT IN INR (IN WORDS)

## BOQ (A-CIVIL)
BILL OF QUANTITY: CIVIL WORKS: Part-A
S. No. | Description of Items | Unit | QTY. | Rate in Figure (in INR) | Rate in Words (in INR) | Amount (in INR)
EARTH WORK
1 | Excavation in all types and sizes of foundations, trenches and drains or for any other purpose with all lead and lift including seperation of usefull soil for refilling including stacking & levelling of same, and disposal of surplus excavated stuff and spoils beyond NRDA boundries or as directed by Engineer In-charge including shoring, dewatering, surface dressing, etc.., complete as per direction of Engineer In-charge.
a | In all types of soil | cum | 12964.3967 |  |  | 0
2 | Providing and filling in plinth in under floor in layers not exceeding 20cm in depth consolidating each deposited layer by ramming and watering, including dressing etc. complete.
a | with sand/ Crusher | cum | 143 |  |  | 0
b | with Hard Mooram | cum | 143 |  |  | 0
3 | Filling from available excavated stuff (Excluding rock) in trenches, plinth, sides of foundation etc. in layers not exceeding 20cm in depth consolidating each deposited layer by ramming and watering from deposited stack spoils as per direction of Engineer In-charfge. | Cum | 5127.4034 |  |  | 0
4 | Supplying chlorpyriphos/ Lindane emulsifiable concentrate of 20% in sealed containers including delivery as specified. | Ltrs. | 2909.2747 |  |  | 0
5 | Diluting chemical emulsion (Chlorpyriphos/ lindane) in water as per manufacturers recommendation and injecting for pre-constructional curative cum preventive anti-termite treatment:(Five year service guarantee bond to be signed by contractor)
a | Surface treatment by spreading emulsion under floor, over the plinth area before laying base concrete @ 5 litres / sqm. | Sqm | 2540.6767 |  |  | 0
b | Treatment of inside of plinth masonry wall on using diluted chemical emulsion @ 1.5 litre per hole, including drilling 12 mm diameter holes in plinth wall below plinth protection at the intervals of 300 mm and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand). | metre | 184.3 |  |  | 0
c | Treatment of outer side of plinth masonry wall using diluted chemical emulsion @ 1.5 litre per hole, including drilling 12 mm diameter holes in plinth wall at the junction of floor at the intervals of 300 mm and plugging with cement mortar 1 :2 (1 cement : 2 Coarse sand). | metre | 184.3 |  |  | 0
FORM WORK
6 | Providing and fixing formwork including centering, shuttering, strutting, staging, propping bracing etc. complete and including its removal at all levels, for:
a | Foundations, footings, base of columns and plinth beam in any shape and size. | Sq.M | 1974.663 |  |  | 0
b | Wall of any thickness including attached pilasters, buttresses etc. | Sq.M | 5157.91 |  |  | 0
c | Beams, lintels, cantilevers & walls | Sq.M | 11803.714 |  |  | 0
d | Columns, rectangular or square in shape | Sq.M | 4271.937 |  |  | 0
e | Stair cases of all types including risers and landings | Sq.M | 563.83 |  |  | 0
f | Suspended floors, roofs and balconies (plain surfaces) | Sq.M | 8448.3306 |  |  | 0
g | Weather shade, chhajja, Cornices and mouldings | Sq.M | 1701.596 |  |  | 0
PLAIN & REINFORCED CEMENT CONCRETE
7 | Providing and laying design mix reinforcement cement concrete with crushed graded stone aggregate 20mm nominal size using batching plant, transit mixer and concrete pump, in all works upto floor five level excluding cost of reinforcement and form work.
a | M-25(using minimum cement 420 kg/cum concrete) | Cum | 5491.3073 |  |  | 0
b | M-20 (using minimum cement 390 kg/cum concrete) | cum | 202.6004 |  |  | 0
8 | Providing and placing in position thermo-mechanically treated (TMT) steel reinforcement for RCC work including cutting, bending, binding etc. complete as per drawings including cost of binding wire and including all wastages etc. complete. | Kg | 739035.35 |  |  | 0
9 | Providing and mixing water proofing material in PCC/ RCC work in the proportion recommended by the manufacturer | kg | 32225.3461 |  |  | 0
10 | Providing and laying nominal mix cement concrete with crushed stone aggregate using concrete mixer in all works upto floor five level excluding cost of form work.
a | 1:4:8 (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size). | Cu.M. | 787.416 |  |  | 0
b | 1:3:6(1cement :3 coursed sand : 6 graded stone aggregate 20mm nominal size ) | cum | 47.7824 |  |  | 0
11 | Providing and laying design mix plain cement concrete with crushed graded stone aggregate 20mm nominal size using batching plant, transit mixer and concrete pump, in all works upto floor five level excluding cost of form work.
a | M-20 (using minimum cement 325 kg/cum concrete) | cum | 31.82 |  |  | 0
12 | Extra for precast PCC/ RCC work of any mix including form work, hoisting and fixing in Cement Mortar. 1:2 (1 Cement : 2 coarse sand) and finishing with cement plaster in Cement Mortar 1:3 (1 Cement : 3 coarse sand) but excluding reinforcement. | cum | 39.345 |  |  | 0
WATER PROOFING WORK
13 | Providing and laying integral cement based treatment for water proofing on horizontal surface at all depth below ground level for under ground structures using rough Kota stone and consisting of: | Sqm | 2076.4697 |  |  | 0
i) 1st layer of 22mm to 25mm thick approved rough Kota stone slab over a 25mm thick base of cement mortar 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound conforming to IS:2645 over the levelling course (levelling course to be paid separately). Joints sealed and grouted with cement slurry mixed with water proofing compound.
ii) 2nd layer of 25mm thick cement mortar 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound.iii) Finishing top with stone aggregate of 10mm to 12mm nominal size spreading @ 8 cudm/sqm thoroughly embedded in the 2nd layer.
14 | Providing and laying integral cement based treatment for water proofing on the vertical surface at all levels by fixing 22 mm to 25mm thick rough Kota stone slab with cement slurry mixed with water proofing compound conforming to IS:2645 with a gap of 20mm (minimum) between stone slabs and the receiving surfaces and filling the gaps with neat cement slurry mixed with water proofing compound and finishing the exterior of stone slab with 20mm thick cement mortar 1:3 (1 cement : 3 coarse sand) with neat cement punning mixed with water proofing compound complete. | sqm | 1056.186 |  |  | 0
15 | Providing and laying water proofing treatment to vertical and horizontal surfaces of depressed portions of WC, kitchen and the like consisting of: | sqm | 773.418 |  |  | 0
i) 1st course of applying cement slurry @ 4.4 Kg/sqm mixed with water proofing compound conforming to IS 2645 including rounding off junction of vertical and horizontal surface.
ii) 2nd course of 20mm cement plaster 1:3 (1 cement : 3 coarse sand) mixed with water proofing compound including rounding off junction of vertical and horizontal surface.
iii) 3rd course of applying blown or residual bitumen applied hot @ 1.7 Kg. per sqm of area.
iv) 4th course of 400 micron thick PVC sheet. (Overlaps at joints of PVC sheet should be 100 mm wide and pasted to each other with bitumen @ 1.7 Kg. per sqm of area.
16 | Providing and laying integral cement based water proofing treatment on roofs, balconies, terraces etc with average thickness of 120mm and minimum thickness at khurra as 65 mm, consisting of following operations including surface preparation:
i) Applying a slurry coat of neat cement using 2.75 kg/sqm. of cement mixed with water proofing compound conforming to IS. 2645 over the RCC slab including adjoining walls upto 300mm height.
ii) Laying brick bats with mortar using broken bricks/brick bats 25 mm to 115mm size with 50% of cement mortar 1:5 (1 cement : 5 coarse sand) mixed with water proofing compound conforming to IS : 2645 over 20 mm thick layer of cement mortar of mix 1:5 (1 cement :5 coarse sand ) mixed with water proofing compound conforming to IS : 2645 to required slope and treating similarly the adjoining walls upto 300 mm height including rounding of junctions of walls and slabs.
iii) After two days of proper curing applying a second coat of cement slurry using 2.75kg/ sqm of cement admixed with water proofing compound conforming to IS : 2645.
iv) Finishing the surface with 20 mm thick joint less cement mortar of mix 1:4 (1 cement :4 coarse sand) mixed with water proofing compound conforming to IS : 2645 including laying glass fibre cloth of approved quality in top layer of plaster and finally finishing the surface with trowel with neat cement slurry and making pattern of 300x300 mm square 3mm deep.
| v) The whole terrace so finished shall be flooded with water for a minimum period of two weeks for curing and for final test. All above operations to be done in order: | sqm | 2134.727 |  |  | 0
ROOFING AND CEILING
17 | Providing and fixing false ceiling with frame work consisting of main and cross runners of anodised aluminium tees of sizes 38mmx25.5mmx1.5mm or equivalent size of angles connected with the help of aluminium elbows/ angles by means of screws/nuts and bolts of required size to form a grid of not more than 610mmx610mm together with anodised aluminium angle of 38mmx38mmx1.5mm size with teak wood plugs and M.S. screws 750 mm centre to centre fixed to the walls and supporting the entire frame work with ceiling by mean of 6mm dia M.S. hangers space between roof and ceiling upto one metre bent to the required shape and M.S. holding cleats of M.S. flats 25mmx6mm painted with one coat of red oxide paint complete of 1220mm centre to centre on either direction and cutting R.C.C. slab and repairing the same in C.M. 1:3 after hanging/ connecting M.S. to the main reinforcement including supplying fixing over aforesaid frame with ceiling tiles.
a | 12 mm thick half random perorated tiles Perforated area 13% | sqm | 5703.681 |  |  | 0
18 | Providing and fixing at all height false ceiling consisting of frame work "W" / "U" / "L" sections made of G.I. sheet with zinc coating of grade 120 consisting of angle cleats of size 25mm wide x 1.6mm thick with flanges of 22mm and 37mm at 1200mm centre to centre one flange fixed to the ceiling with dash fastener 12.5mm diax40mm long with 6mm dia bolts to the angle hangers of 25x25x0.55mm of required length, and other end of angle hanger being fixed with nut and bolts to G.I. channels 45x15x0.9mm running at the rate of 1200mm centre to centre to which the ceiling section 0.5mm thick button wedge of 80mm with tapered flanges of 26mm each having clips of 10.5mm at 450mm centre to centre shall be fixed in a direction perpendicular to G.I. channel with | Sqm | 1161.608 |  |  | 0
connecting clips made out of 2.64mm diax230mm long G.I. wire at every junction including fixing the gypsum board with ceiling section and perimeter channels 0.55mm thick 27mm high having flanges of 20mm and 30mm long, the perimeter of ceiling fixed to wall/partition with the help of rawl plugs at 450mm centre to centre with 25mm long drive-all screws @ 230mm interval including jointing and fixing to a flush finish of tapered and square edges of the board with recommended filler, jointing tapes, finisher and two coats of primer suitable for board as per manufactures specification and also including the cost of making openings for light fittings, grills, diffusers, cutouts made with frame of perimeter channels suitably fixed all complete as per drawing and specification and direction of the Engineer in Charge but excluding the cost of painting with 12.5 mm thick tapered edge gypsum board conforming to IS: 2095- Part I.
19 | Providing and fixing IS: 3564 marked Aluminium die cast body tubular type universal hydraulic door closer with necessary accessories and screws etc complete. | each | 96 |  |  | 0
20 | Providing and fixing of six/seven levers branded and approved mortise lock. | each | 81 |  |  | 0
21 | Designing, providing and fixing aluminium frame work made of special aluminium section on building face with M.S. angle iron brackets fixed on RCC structure with S.S. hold fasteners, including providing and fixing two sided structural adhesive tape of appropriate grade (NORTON or equilent), on aluminium sections for fixing aluminium/ glass panel, sealing on periphery of frame work, by providing EPDM gasket, silicon weather sealant between aluminium frame and building structure including hire charges of double scaffolding complete. | KG | 5817.42 |  |  | 0
22 | Providing and fixing aluminium composite panels in approved panel sizes, thickness and shape on aluminium frame work on face of building. (Frame to be paid for separately)
a | 4mm thick | Sqm | 107.73 |  |  | 0
23 | Providing and fixing laminated glass sheet of 8.76mm thickness in approved sizes on aluminium frame work on face of building. (Frame to be paid for separately). | Sqm | 545.832 |  |  | 0
BRICK WORK
24 | Brick work with modular fly-ash lime bricks (FALG Bricks) confirming to IS:12894-2002 of class designation 35 in foundation and plinth & super structure in;
a | Cement Mortar 1:5 (1 cement : 5 coarse sand) | Cum | 16.56 |  |  | 0
b | Cement Mortar 1:5 (1 cement : 5 coarse sand)
Extra for brick work in superstructure:
i | Above plinth and upto floor five level. | Cum | 1208.7 |  |  | 0
25 | Item Deleted
a
26 | Brick work with modular fly-ash lime bricks 100mm thick wall (FALG Bricks) confirming to IS:12894-2002 of class designation 35 in superstructure Above plinth and upto floor five level
a | Cement Mortar 1:4 (1 cement : 4 coarse sand) | Sqm | 4745.3563 |  |  | 0
27 | Extra for providing and placing in position hopping 25x1.60 mm or 2 Nos 6mm dia MS bars reinforcement at every third course of half brick masonry. | Sqm | 4745.3563 |  |  | 0
WOOD WORK
28 | Providing and fixing exterior grade type & phenoformaldehyde bound flush door shutters decorative type, core of block board construction with frame of first class hard wood and well matched teak ply veneering with vertical grains or cross bands and face veneers on both faces of shutters excluding hinges.
a | 35mm thick (Single leaf)phenoformaldehyde bound flush door | Sqm | 428.2 |  |  | 0
29 | Extra for double leaf shutter instead of single leaf. | Sqm | 116.55 |  |  | 0
30 | Extra for cutting rebate in flush door shutter (total area of door shutter to be measured). | Sqm | 116.55 |  |  | 0
31 | Providing and fixing in position doors, windows and ventilators frames made of cold rolled pressed steel sheet framed profiles made from commercial M.S. Sheets conforming to I.S. 513 of 1973 and as per general specifications of I.S 4351 including hinges jamb, lock jamb, steel butt hinges, base tie, joints mitred and welded with 10cm long legs of size 15x3mm M.S. flat, embedded in cement concrete blocks 15x10x10cm size of grade M-10 or rawl plugs and screws or with fixing clips or with bolts and nuts including neatly compacted filling M-10 cement concrete in profile section applying a priming coat of red oxide zinc chromate primer.
a | Single rebate 100mmx50mm size, 1.6mm thick sheet. | Mtrs. | 1350.2 |  |  | 0
32 | Providing and fixing 35mm thick glazed shutter frames for windows, clerestory windows, ventilators etc using glass panes including M.S. butt hinges with necessary screws but excluding glass panes. (Area of shutter to be measured without deducting panelling area).
a | Teak wood | sqm | 100.818 |  |  | 0
33 | Providing and fixing glass panes in glazed or panelled and glazed shutters of doors and window, clerestory windows etc (area of shutter to be measured in case of full glazed shutter).
a | 5mm thick | sqm | 76.131 |  |  | 0
34 | Providing and fixing aluminium sliding door bolts ISI marked anodised(anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with nuts and screws etc. complete :
a | 300x16mm | Each | 36 |  |  | 0
b | 250x16mm | Each | 370 |  |  | 0
35 | Providing and fixing aluminium tower bolts ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868 ) transparent or dyed to required colour or shade with necessary screws etc. complete :
a | 250x10mm | Each | 77 |  |  | 0
b | 200x10mm | Each | 2317 |  |  | 0
36 | Providing and fixing aluminium handles ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc. complete :
a | 125 mm | Each | 2694 |  |  | 0
37 | Providing and fixing brass door latch with brass polished MS screws complete:
a | 300x16x5 mm | Each | 268 |  |  | 0
38 | Providing and fixing aluminium hanging floor door stopper ISI marked anodised (anodic coating not less than grade AC 10 as per IS : 1868) transparent or dyed to required colour or shade with necessary screws etc. complete :
a | Twin rubber stopper | Each | 313 |  |  | 0
39 | Providing and fixing stainless steel fixed stopper with necessary stainless steel screws complete.
a | 60 mm long | Each | 313 |  |  | 0
40 | Providing and fixing factory made P.V.C. door frame of size 50x47mm with a wall thickness of 5mm, made out of extruded 5mm rigid PVC foam sheet mitred at corners and joined with 2 Nos of 150mm long brackets of 15x15mm M.S. square tube, the vertical door profiles to be reinforced with 19x19mm M.S. square tube of 19 gauge, EPDM rubber gasket weather seal to be provided through out the frame. The door frame to be fixed to the wall using M.S. screws of 65/100mm size complete as per manufacturers specification and direction of Engineer-in-Charge. | Mtrs. | 326.7 |  |  | 0
41 | Providing and fixing 30mm thick factory made panel PVC door shutter consisting of frame made out of M.S. tubes of 19 gauge thickness and size of 19mm x 19mm for styles and 15x15mm for top & bottom rails. M.S. frame shall have a coat of steel primers of approved make and manufacture . M.S. frame covered with 5mm thick heat moulded PVC 'C' channel of size 30mm thickness, 70mm width out of which 50mm shall be flat and 20mm shall be tapered in 45degree angle on either side forming styles; and 5mm thick, 95mm wide PVC sheet out of which 75mm shall be flat and 20mm shall be tapered in 45 degree on the inner side to form top and bottom rail and 115mm wide PVC sheet out of which 75mm shall be flat and 20mm shall be tapered on both sides to form lock rail. Top, bottom and lock rails shall be provided either side of the panel. 10mm (5mm x 2 ) thick, 20mm wide cross PVC sheet be provided as gap insert for top rail & bottom rail. paneling of 5mm thick both side PVC sheet to be fitted in the M.S. frame welded/ sealed to the styles & rails with 7mm (5mm+2mm) thick x 15mm wide PVC sheet beading on inner side, and joined together with solvent cement adhesive. An additional 5mm thick PVC strip of 20mm width is to be stuck on the interior side of the 'C' Channel using PVC solvent adhesive etc. complete as per Manufacturer’s specification including 3 nos ISI marked stainless steel hinges of size 100x58x1.9 mm complete. (for W.C. and bathroom door shutter).
a | Both side Pre-laminated panel PVC door shutter | Sqm | 103.96 |  |  | 0
STEEL AND ALUMINIUM WORK
42 | Providing stainless steel railing/ grill made of S.S.(Grade 304Min.). flats, hollow S.S. pipe or square/ rectangular sections of approved design fixing in stair case, balcony or other places with metal fasteners and stainless steel bolts etc complete. | Kg | 3564 |  |  | 0
43 | Providing and fixing steel door with M.S. sheet 1.6mm thick, frame of angle iron, diagonal braces of angle/ flat iron of suitable size, 3.00 mm M.S. gusset plates at junctions and corners, all necessary fittings complete including applying a priming coat of red oxide zinc chromate primer.. | Kg | 1233 |  |  | 0
44 | Providing and fixing M.S. grill of approved pattern made of M.S. flats or square or round bars welded to steel frame of windows etc. including applying a priming coat of red oxide zinc chromate primer | Kg | 24337.0725 |  |  | 0
45 | Providing and fixing factory made ISI marks steel doors, windows and ventilators side/ top/ centre hung made up of standard rolled steel section conforming to IS 1038:1968 and IS1977:1969 joints mitred and flash butt and sash bars tenoned and riveted/ welded with 10 cm long lugs of size 15x3mm embedded in cement concrete block 15x10x10 cms of 1:3:6 (1 cement :3 Coarse sand: 6 graded stone aggregate 20 mm nominal size) or rawl plugs and screws or with bolts and nuts as required including providing and fixing of hinges, pivots, handles, pegs, stays, rolling devices, locking arrangements, spring catch etc., as required complete including applying a priming coat of red oxide zinc chromate primer. | Kg | 101.25 |  |  | 0
46 | Providing and fixing aluminium work for doors, windows, ventilators and partitions made out of extruded aluminium standard sections (main section with minimum 1.5mm thickness) conforming to IS: 733, IS: 1285 mitred and jointed mechanically including aluminium cleats, neoprene weather stripping gasket beveled edge beading, screws duly fixed in wall/ floor with fixing clips or hold fasteners or bolts and nuts as required aluminium sections shall be anodized transparent or dyed to approved shade according to IS: 1868, minimum anodic coating shall be of grade AC-15. (Glazing and panelling to be paid for separately
a | For fixed portion | KG | 540 |  |  | 0
b | For shutter of doors, windows & ventilators including providing and making provision for fixing of fitting wherever required including the cost of PVC/ neoprene gasket required (Fittings shall be paid for separately). | KG | 8216.1 |  |  | 0
47 | Providing and fixing glazing in aluminium door, window, ventilator shutters and partitions etc. with PVC/ neoprene gasket etc. complete. (Cost of aluminium snap beading shall be paid in basic item):
a | With float glass panes of 5mm thickness | Sqm | 880.47 |  |  | 0
48 | Structural steel work riveted or bolted or welded in built-up sections, trusses and frames work upto a height of 5m above plinth level, including cutting, hoisting, fixing in position and applying a priming coat of red oxide zinc chromate primer. | Kg | 12555.6 |  |  | 0
49 | Supplying and fixing rolling shutter of approved makes made of M.S. laths interlocked together through their entire length and jointed together at the end by end locks, mounted on specially designed pipe shaft with brackets, side guides and arrangements for inside and out side locking with push and pull arrangement complete but excluding the cost of top cover and spring.
a | 80x1.25mm M.S. Laths | Sq.M | 9 |  |  | 0
50 | Providing and fixing 27.5cm long wire spring for rolling shutters. | each | 4 |  |  | 0
51 | Providing and fixing M.S. sheet top cover for rolling shutter
a | 1.25mm thick | sqm | 2.7 |  |  | 0
52 | Providing and fixing ball bearing for rolling shutters. | each | 4 |  |  | 0
53 | Providing and fixing M.S. fan clamp/ hook for ceiling fan made out of 16 mm dia M.S. bar bent to shape with hooked ends in R.C.C. slabs, beams during laying including painting the exposed portion of loop. | Each | 560 |  |  | 0
PLASTERING AND POINTING
54 | 12mm thick cement plaster of Mix
a | In Cement Mortar 1:4 (1 cement : 4 fine sand) | Sq.m | 33993.7128 |  |  | 0
55 | 18 mm thick cement plaster with under layer of 12mm thick cement plaster 1:5 (1 cement : 5 fine sand) finished with a top layer of 6mm thick cement plaster 1:3 (1 cement : 3 fine sand). | Sq.m | 7036.1592 |  |  | 0
56 | 6mm thick cement plaster
a | In cement mortar 1:3 | Sq.m | 11460.6151 |  |  | 0
57 | Neat cement punning | Sq.m | 2175.7482 |  |  | 0
58 | 12mm thick plain cement mortar bands in cement mortar 1:4 (1 cement : 4 fine sand) per cm width:
a | Flush band | Mtrs. | 10000 |  |  | 0
b | Sunk band | Mtrs. | 10000 |  |  | 0
c | Raised band | Mtrs. | 10000 |  |  | 0
59 | Providing and fixing chicken mesh weighting not less than 250 gms/ sqm as per IS : specification in the required width with 10mm long steel nails on vertical and horizontal surface near R.C.C. and brick walls junctions including scaffolding and all lead and lifts etc. complete before plastering upto 10mts in height. | Sq.m | 10354.3925 |  |  | 0
60 | Extra for plastering of exterior walls when height exceeds 10m above ground level for every additional height of 3.0m or part thereof. | Sq.m | 3558.2626 |  |  | 0
FLOORING
61 | 52 mm thick cement concrete flooring with under layer of 40mm thick cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) and top layer of 12 mm thick cement metallic hardener concrete mix 1:2 (1 cement hardener mix : 2 stone aggregate of 6 mm size by volume) with metallic hardening compound of approved quality mixed with cement in ratio of 4:1 (4 cement : 1 metallic floor hardening compound by weight) including finishing etc. complete. | sqm | 2307.8337 |  |  | 0
62 | Extra for making chequers of approved pattern on cement concrete flooring, landing, pavement etc. | sqm | 2298.8337 |  |  | 0
63 | Cement plaster skirting upto 30 cm. height with cement mortar 1:3 (1 cement : 3 fine sand) finished with a floating coat of neat cement including rounding of junction with floor.
a | 18 mm thick in two layers of 12mm and 6mm | sqm | 27.645 |  |  | 0
64 | 15 mm thick Table rubbed polished Granite stone slab in risers and treads of steps skirting dado and pillars laid on 12mm (average) thick base of cement mortar 1:3 (1 cement : 3 coarse sand) and jointed with grey cement slurry including rubbing and polishing etc. complete (single stone is to be used for risers and treads of steps and width of stone for skirting and dado shall be equal to the height of skirting & dado and length of 1.0 m).
a | Granite stone black | sqm | 513.6 |  |  | 0
65 | 15mm thick Granite work (machine cut, table rubbed & mirror polished) for wall lining (veneer work) in cement mortar 1:3 (1 cement : 3 coarse sand) including pointing with cement mortar 1:2 (1 white cement: 2 marble dust) mixed with matching pigment. (Area of slab should be over 0.5 sqm).
a | Granite stone lakha red/ shahi red | Sqm | 172.44 |  |  | 0
b | Granite stone black | Sqm | 31.2 |  |  | 0
66 | Extra for nosing in Granite stone for treads. | Rmts | 150.4 |  |  | 0
67 | Providing and laying ceramic ANTISKID floor tiles 600x600mm conforming to IS : 15622 of approved make, colour, shade laid on 20 mm thick Cement Mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement mixed with matching pigment etc., complete. | Sqm | 412.34 |  |  | 0
68 | Providing and fixing ceramic glazed wall tiles conforming to IS : 15622 of approved make, colours, shades and 450X300mm size on wall and dados over 12 mm thick bed of cement Mortar 1:3 (1 cement : 3 coarse sand) and jointing with grey cement slurry @ 3.3kg per sqm including pointing in white cement mixed with matching pigment complete. | Sqm | 2051.701 |  |  | 0
69 | Providing and laying antiskid exterior design floor tiles (Ultra tiles) 20mm-25mm thick (M40 Grade) conforming to IS : 15622 of approved make, colour, shade laid on 20 mm thick Cement Mortar 1:4 (1 cement : 4 coarse sand) including pointing the joints with white cement mixed with matching pigment etc., complete. | Sqm | 329.715 |  |  | 0
70 | 25 mm thick KOTA stone slab flooring over 20mm (average) thick base of cement mortar 1:4 laid over and jointed with grey cement slurry mixed with pigment to match the shade of the slab including grinding rubbing and polishing etc. complete (Area of slab to be over 0.20 sq.m and upto 0.50 sq.m) | Sqm | 4451.6 |  |  | 0
71 | KOTA stone slab 25mm thick in risers and treads of steps, skirting dado and pillar laid in 12mm (average) thick cement mortar 1:3 (1 cement : 3 coarse sand) and jointed with grey cement slurry mixed with pigment to match the shade of the slab including rubbing and polishing complete. (single stone is to be used for riser and treads of steps and the width of stone for skirting and dado shall be equal to the height of skirting/ dado with a minimum length of 1.0 M.) | Sqm | 30.963 |  |  | 0
72 | 15mm thick Granite work (machine cut, table rubbed & mirror polished) for kitchen platform, vanity counters, window sills and similar locations of required size laid over 20mm thick base cement mortar 1:4 (1 cement : 4 coarse sand) including joints treated with white cement mixed with matching pigment including rubbing and polishing to edge moulding to give high gloss finish.
a | Granite Stone Black | Sqm | 74.69 |  |  | 0
73 | Extra for providing edge moulding to 15mm thick stone counters, vanities etc. including machine polishing to edge to give high gloss finish etc. complete as per design approved by Engineer-in-Charge.
a | Granite work | Rmts | 971.8 |  |  | 0
74 | Providing and laying vitrified floor tiles with double charge/ multi charge printing with water absorption less than 0.5% and conforming to IS : 15622 of approved make in all colours and shades and size mentioned below (+/- 10mm), laid on 20mm thick cement mortar 1:4 (1 cement : 4 coarse sand) including grouting the joints with white cement and matching pigments etc. complete:
a | Size 600x600mm | Sqm | 2371.1 |  |  | 0
WHITE WASH, COLOUR WASH, DISTEMPERING, PAINTING
75 | Painting on new work (two or more coats) to give an even shade with: |  | 0
a | Satin synthetic enamel paint (top most approved branded quality) | Sq.M | 1107.9925 |  |  | 0
76 | Wall painting with acrylic luxury emulsion (plastic) paint (top most approved branded quality) to give an even shade.
a | On new work (two or more coats) | Sq.M | 33631.4528 |  |  | 0
77 | Applying one coat of cement primer on wall surface. | Sq.M | 27262.0964 |  |  | 0
78 | Providing and applying 2mm thick ready mix exterior grade putty (Birla wall care, Alltek Superfine W/R of (NCL), J.K. wall putty) on walls to make the surface smooth and even. | Sq.M | 33549.2864 |  |  | 0
79 | Painting new exterior surface (two or more coats) with PREMIUM TEXTURED paint as per manufacturer's specifications to give protective and decorative finish including cleaning washing of surface etc. complete with: | Sq.M | 6418.4092 |  |  | 0
80 | Providing and laying french sprit polish on new wood work after preparing the surface by rubbing down smooth with sand papers, covering the knots, if visible, applying a coat of wood filler, cleaning the surface, applying 50 or more coats of french spirit polish till the surface gives high gloss. | Sq.M | 88.81 |  |  | 0
81 | Providing and fixing expanded polyethyle backer rod of desired Diameter having min.density 22kg/cm as per ASTM D-3575 & compression strength of .4kg/sqm as per( ASTM 5249 ) diameter 25% greater than the necessary joint width the joint is to be filled with approx. silicone / polysulphide sealent as dia. called for I/Call incidents etc. complete | RM | 669.68 |  |  | 0
82 | Providing and fixing in position impregnated fibre board confirming to IS: 1838 in expansion joints, including cost of primer, sealing compound all complete.
a | 25 mm thick | Sqm | 347.524 |  |  | 0
83 | Providing and fixing aluminium strip 1.60 mm thick on expansion joints with iron screws as per design to match the colour, shade of wall treatment . | Sqm | 244.744 |  |  | 0
84 | Providing & Filling Brick Bats in sunken portion of toilet with sand Including dressing etc. complete | Cum | 190.283 |  |  | 0
85 | Item Deleted
SUB TOTAL OF PART A : CIVIL WORK | [5 empty] | 0

## BOQ (B-ROAD)
BILL OF QUANTITY : ROAD WORKS: PART-B
S. No | Description of Items | Unit | QTY. | Rate in Figure (in INR) | Rate in words (in INR) | Rate in Words (in INR) | Amount (in INR)
1 | Construction of embankment / sub grade with Material Obtained from Borrow Pits (Construction of embankment with approved material/selected soil having C.B.R. > 5 (unless specified otherwise in the contract) obtained from borrow pits with all lifts and leads, transporting to site, spreading, grading to required slope and compacting to meet requirement of table 300-2) | CUM | 432 |  |  | 0
2 | Construction of granular sub-base by providing close graded Material, carriage of mixed Material to work site, spreading in uniform layers with motor grader on prepared surface watering, rolling and compacting with vibratory power roller at OMC to achieve the desired density, complete as per clause 401
Plant mix method
a | for grading-III Material | CUM | 216 |  |  | 0
3 | Dry Lean Cement Concrete Sub- base (Construction of dry lean cement concrete Sub- base over a prepared sub-grade with coarse and fine aggregate conforming to IS: 383, the size of coarse aggregate not exceeding 25 mm, aggregate cement ratio not to exceed 15:1, aggregate gradation after blending to be as per table 600-1, cement content not to be less than 150 kg/ cum, optimum moisture content to be determined during trial length construction, concrete strength not to be less than 10 Mpa at 7 days, mixed in a batching plant, transported to site, laid with a paver with electronic sensor, compacting with 8-10 tonnes vibratory roller, finishing and curing.) | CUM | 209.25 |  |  | 0
4 | Cement Concrete Pavement (Construction of un-reinforced, dowel jointed, plain cement concrete pavement over a prepared sub base with 43 grade cement @ 400 kg per cum, coarse and fine aggregate conforming to IS 383, maximum size of coarse aggregate not exceeding 25 mm, mixed in a batching and mixing plant as per approved mix design, transported to site, laid with a fixed form or slip form paver, spread, compacted and finished in a continuous operation including provision of contraction, expansion, construction and longitudinal joints, joint filler, separation membrane, sealant primer, joint sealant, debonding strip, dowel bar, tie rod, admixtures as approved, curing compound, finishing to lines and grades as per drawing) | CUM | 209.25 |  |  | 0
5 | Cast in Situ Cement Concrete M20 kerb (Construction of cement concrete kerb with top and bottom width 115 and 165 mm respectively, 300 mm high in M 20 grade PCC on M-10 grade foundation 150 mm thick, foundation having 50 mm projection beyond kerb stone, kerb stone laid with kerb laying machine, foundation concrete laid manually, all complete as per clause 408) | METER | 450 |  |  | 0
6 | Painting on Concrete Surfaces
a | Two coats on new surfaces (Painting two coats after filling the surface with synthetic enamel paint in all shades on new plastered concrete surfaces) | SQM | 209.25 |  |  | 0
7 | Painting Lines, Dashes, Arrows etc on Roads in Two Coats on New Work (Painting lines, dashes, arrows etc on roads in two coats on new work with ready mixed road marking paint conforming to IS:164 on bituminous surface, including cleaning the surface of all dirt, dust and other foreign matter, demarcation at site and traffic control )
(i) | Up to 10 cm in width | SQM | 122.85 |  |  | 0
8 | Precast interlocking premium concrete paver blocks: Providing & laying factory made confirm technical specification of Bureau of Indian Standards 15658 of 2006 of heavy duty pavers resulting in consistent and uniform quality, rubber moulded, white cement based , pigmented block lacquer coating and cured through drying process mechanically vibrated and compacted precast interlocking premium concrete paver blocks in M40 grade , 60mm thickness of approved size, design and colour with providing and laying in position over 40 mm thick average complete coarse sand bed with joints of 3mm thick filled by fine sand including leveling with surface vibrator, temping and sweeping etc. complete.
a | Plain or coloured precast interlock concrete block | Sqm | 675 |  |  | 0
9 | Providing & laying Reinforced cement concrete pipe NP-3/ prestressed concrete pipe for culverts including fixing coller with cement mortar 1:2 of dia 450mm. | RM | 48 |  |  | 0
SUB TOTAL OF PART B : ROAD WORK | [5 empty] | 0

## BOQ (C-ELECTRICAL)
BILL OF QUANTITY: ELECTRICAL WORK : PART-C
S.No. | Description of Items | Unit | QTY. | Rate in Figure (in INR) | Rate in words (in INR) | Amount (in INR)
HV CABLE LAYING (33 KV) (Single Cable)
1 | Supplying and laying one number following sizes XLPE, steel armoured, aluminium conductor power cable of 33 KV grade direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required.
a | 3 x 95 sq mm | mtr | 100 |  |  | 0
2 | Supplying and making indoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminum conductor cable of 33 KV grade as required.
a | 95 sq. mm | Each | 4 |  |  | 0
3 | Supplying and making outdoor cable end termination with heat shrinkable jointing kit complete with all accessories including lugs suitable for following size of 3 core, XLPE aluminum conductor cable of 33 KV grade as required.
a | 95 sq. mm | Each | 3 |  |  | 0
HT PANEL
4 | HT panels inside the Receiving substation: Supplying, Erection, Testing and Commissioning of 33 KV extensible type Panel Board suitable for indoor installation for use on 33 KV earthed system having a symmertrical breaking capacity of 60 MVA for 1 Sec. at 33 KV comprising. The panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 1 |  |  | 0 | 0
INCOMING
33KV, 25KA 2.5MM CRCA 1NO
ENCLOSURE WITH COPPER BUSBAR BOTH 1 NO
HORIZONTAL AND VERTICAL RUNS,
CONTROL WIRING & MISCELLANOUS ITEM
2.5MM CRCA INDOOR ENCLOSURE
DOOR SYSTEM
CIRCUIT BREAKER
33KV, 630A VCB OUTDOOR WITH RKG HANDLE 1 NO WITH 24 VOLT BATTERY & CHARGER 2 Nos.
CONTROL VOLTAGE: 230VAC
AUX VOLTAGE: 24 V DC
CURRENT TRANSFORMER
CAST RESIN CT’S OF RATIO ---120/60/5A 2 NO
CL 1.0 / 5P10, 15 VA
POTENTIAL TRANSFORMER
CAST RESIN PT’S OF RATIO 1 NO
33KV/110V, CL 1.0, 100VA
√ 3 √3
LED
RED INDICATING LAMP 1 NO
YELLOW INDICATING LAMP 1 NO
BLUE INDICATING LAMP 1 NO
GREEN INDICATING LAMP 1 NO
RELAY-CTR 5A, AUX.24V DC
PHASE OVERCURRENT RELAY 1 NO
NUMERICAL IDMT RELAY WITH O/C & E/F ELEMENT 1 NO
OUTGOING PANEL
33KV, 25 KA 2.5MM CRCA 3 NO
ENCLOSURE WITH COPPER BUSBAR BOTH 1 NO
HORIZONTAL AND VERTICAL RUNS,
CONTROL WIRING & MISCELLANOUS ITEM
2.5MM CRCA INDOOR ENCLOSURE
DOOR SYSTEM
BUS COUPLER
MISCELLANOUS
HOOTER/ BUZZER 1 NO
2 POLE, 25A SPRING RETURN TO NEUTRAL - BCS 1 NO
LOCAL/ REMOTE SWITCH - 6A, 2 WAY 1 NO
SPACE HEATER - 100W 1 NO
THERMOSTAT - 30 TO 1100c 1 NO
EMERGENCY PUSH BOTTON 1 NO
8 WINDOW ANNUNCIATOR 1NO
METERS
DIGITAL VAF METER (DM6100) CL 1.0 1 NO
DIGITAL AMMETER WITH PHASE SELECTOR SWITCH
DIGITAL VOLTMETER WITH PHASE SELECTOR SWITCH
TRANSFORMER/SUBSTATION WORK
5 | Supplying and installation of outdoor type Transformer ONAN type with copper winding having a continuous rating of 500 KVA, 33 KV/415 Volts 3 Phase 50 Hz Vector group DY-11, tapings in steps of ± 2.5%, ± 5%, -7.5% with oil conservator, silica gel breather having connecting terminals on HV side suitable for 3 core 33 KV XLPE aluminium cable connection, cable end box on medium voltage side suitable for 1.1 KV 3½ core UG cable, on double pole structure or Brick /CC/RCC platform with all fittings, accessories, filled with filtered transformer oil including testing and commissioning etc. complete as required. | Each | 2 |  |  | 0
6 | Excavation of pit of size 5'x5'x5', fillng with sand for 4"(10 cm) depth, laying bed concrete with CC (1:4:8) using 40 mm HBG metal for 4" depth, construction of distribution transformer plinth with footing size (5'x5'x4" and 3'x3'x1.5'), coloumn size 9"x9"x8'8", beam size 9"x9"x9'3", slab 5'x5'x4", providing reif steel 12 mm rod (76 kgs) as per the direction of ADE/Civil, refilling the hollow portion with excavated earth, and slabs, coloumn and beam with CM (1:5) 20 mm thick, including cost and transport of all materials and labour charges for all operation with an average lead of 5 KM and lifts etc., complete as directed by the Engineer in charge. | each | 2 |  |  | 0 | 0
7 | Earthing with G.I. earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as required. | set | 6 |  |  | 0
8 | Earthing with copper earth plate 600 mm X 600 mm X 2 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt as required. | Nos. | 6 |  |  | 0
9 | Providing and laying earth connection from earth electrode with 4.00 mm dia copper wire in 15 mm dia G.I. pipe from earth electrode at 0.5 meter depth below ground level including excavation and refilling the trench etc as required. | mtr | 25 |  |  | 0
10 | Providing and fixing 25 mm x 5 mm GI strip on surface or in recess for connections etc as requried. | mtr | 100 |  |  | 0
11 | Providing and fixing 25 mm x 5 mm copper strip on surface or in recess for connections etc as requried. | mtr | 20 |  |  | 0
MV PANEL
12 | MV panels inside the Receiving substation: Supplying, Erection, Testing and Commissioning of 440 V extensible type Panel Board suitable for indoor installation for use on 440/500 KV earthed system having a symmertrical breaking capacity of 50KA. The panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 1 |  |  | 0 | 0
INCOMING
MAIN SWITCH
Draw out type, 415/500 volts, 4 pole air-circuit breaker 800 amps 2 no
MEASURING INSTRUMENT
CAST RESIN CT’S OF RATIO 800/5A 2 NO
CAST RESIN PT’S 2 NO
DIGITAL AMMETER WITH PHASE SELECTOR SWITCH 2 NOS
DIGITAL VOLTMETER WITH PHASE SELECTOR SWITCH 2 NOS
2 SET OF OF PHASE INDICATING LAMP WITH CONTROL MCB
RELAY SET OF AUXILARY, CONTROL MCB WITH SUITABLE QUANTITY AND RATING 2 SET
REVERSE POWER RELAY, NO VOLT RELAY, OVER VOLTAGE RELAY DIFFERENTIAL PROTECTION 1 SET
BUSBAR
60x5 MM 500 A COPPER Bus bar OF 3 NOS. SET 2 nos.
BUS TURNKING OF 1600 AMPS
OUTGOING PANEL
MAIN SWITCH
MCCB 4 POLE 200 A, 50 KA
BUSBAR
60x5 MM 500 A COPPER Bus bar OF 3 NOS. SET 3 nos.
30X5 mm 200 amps
APFC PANEL AT SUBSTATION
13 | INCOMER
| APFC with the max. 400 Kvar rating with busbar incoming microprocessor based release having short circuit, over current, earth fault, under voltage relay. | Set | 1 |  |  | 0 | 0
96 mm square flush pattern digital Voltmeter (0-500 V), accuracy class 1, suitable range for 3 phase, 4 wire operation with LED display and built-in selector switch along with 3 nos. of 2 Amp SP/ MCBs.- 3 Sets.
96 mm sq. Flush pattern Digital Type Ammeter of suitable range (to measure 0-800A), for 3 phase 4 wire operation with LED display and selector switch with 3 numbers of class 1.0 accuracy, 15 VA burden & suitable range CTs.- 3 sets.
3 sets Indication Lamps, LED type for R,Y,B and breaker 'ON', 'OFF', 'TRIP' indications each with 2 Amp MCBs for protection.
BUSBARS
1 set of high conductivity Aluminium bus bars of minimum 800 Amps capacity, TPN with heat shrinkable coloured sleeves and i/c DMC busbars supports at required intervals.
OUTGOINGS
1 Nos. 800A, TPN, 50 kA, MCCB with Microprocessor based release having adjustable over load and adjustable short circuit, auxiliary contact, Rotary handel, spreader link, etc.
Relays, control contactors, Aux.Relays, Timers:
1 No. Microprocessor based AMF logic relay having UV and OV, Phase reversal, engine start relay, engine cranking relay, Auto/ Mannual/ test/ service etc.
1 Set of All other auxiliary relays, auxiliary/ control contactors (24V DC and 230V AC), timers, Three impulse unit, Master trip relay, etc of suitable rating and quantity as required to achieve AMF function as described in technical specifications.
1 Set LED Indication lamps, Push buttons, window annunciation fascia etc of required quantity as per technical specifications.
Metering:
1 set of Digital AC Ammeter of suitable range with built-in selector switch, Cast Resin CTs & control MCBs
1 set of Digital AC Voltmeter of suitable range with built-in selector switch & control MCBs
1 no.Digital Frequency meter
1 No.Digital Power factor meter
1 No. Digital DC Voltmeter
1 No. Digital DC Ammeter
Others
1 set of required quantity of suitable range and accuracy class of Cast Resin CTs for Metering & Protection
1 set of required quantity and rating of HRC fuse for control & protection circuits - 01 Set
Instruments
1 Set R Y B phase indicating lamps with protection fuses.
1 Lot of control wiring.
1 Set of designation plates.
Other items such as:-
Illumination light interlocked with doors.
Suitable Nos. and dia of Exhaust Fan with Temp. rise thermostat.
MV CABLE LAYING
14 | Supplying and laying following sizes one number PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade in the existing RCC/ HUME/ STONEWARE/ METAL pipe as required.
a | 3.5x95 sq.mm. | mtr | 140 |  |  | 0
b | 3.5 x 120 sq. mm. | mtr | 110 |  |  | 0
c | 3.5 x 300 sq. mm. | mtr | 260 |  |  | 0
15 | Supplying and laying following sizes one number PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade in the existing masonry open duct as required.
a | 3.5 x 120 sq. mm. | mtr | 110 |  |  | 0
b | 3.5 x 300 sq. mm. | mtr | 680 |  |  | 0
16 | Supplying and laying following sizes one number PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade on surface/ existing cable tray as required.
a | 4x25 SQ MM | mtr | 300 |  |  | 0
b | 3.5 x 35 sq mm | mtr | 80 |  |  | 0
17 | Supplying and laying following sizes one number PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade on surface/ existing cable tray with M.S. flat clamp and steel dash fastener/ G.I. bolts and nuts as required.
a | 3.5 x 120 sq. mm. | mtr | 360 |  |  | 0
b | 3.5x240 sq.mm. | mtr | 250 |  |  | 0
c | 3.5 x 300 sq. mm. | mtr | 260 |  |  | 0
18 | Supplying and making end termination with brass compression gland and aluminum lugs for following size armoured aluminum conductor power cable of 1.1 KV grade as required.
a | 3½ X 35 sq. mm | Each | 3 |  |  | 0
b | 3½ X 95 sq. mm | Each | 2 |  |  | 0
c | 3½ X 120 sq. mm | Each | 10 |  |  | 0
d | 3½ X 240 sq. mm | Each | 10 |  |  | 0
e | 3½ X 300 sq. mm | Each | 36 |  |  | 0
f | 4 X 25 sq. mm | Each | 4 |  |  | 0
19 | Supplying, fixing and cramping suitable size and all type aluminium ferule/lugs to following size 1.1 KV grade power cable core/lead, pressed with high pressure cramping tool including connection to switch gear/ MCCB etc as required.
a | 3½ X 35 sq. mm | Each | 20 |  |  | 0
LT PANEL
20 | LT panels inside the Receiving substation: Supplying, Erection, Testing and Commissioning of 440 V extensible type Panel Board suitable for indoor installation for use on 440/500 KV earthed system having a symmertrical breaking capacity of 50KA. The panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 1 |  |  | 0 | 0
INCOMING
MAIN SWITCH
Draw out type, 415/500 volts, 4 pole air-circuit breaker 800 amps 1 no
415/500 volts, 4 pole mccb 400 amps 1 no
MEASURING INSTRUMENT
CAST RESIN CT’S OF RATIO 800/5A 2 NO
CAST RESIN PT’S 2 NO
DIGITAL AMMETER WITH PHASE SELECTOR SWITCH 2 NOS
DIGITAL VOLTMETER WITH PHASE SELECTOR SWITCH 2 NOS
2 SET OF OF PHASE INDICATING LAMP WITH CONTROL MCB
RELAY SET OF AUXILARY, CONTROL MCB WITH SUITABLE QUANTITY AND RATING 1 SET
REVERSE POWER RELAY, NO VOLT RELAY, OVER VOLTAGE RELAY DIFFERENTIAL PROTECTION 1 SET
BUSBAR
100x5 MM 1000 A COPPER Bus bar NOS. SET 2 nos.
OUTGOING PANEL
BUSBAR
100x5 MM 1000 A aluminium Bus bar NOS. SET 2 nos.
60x5 MM 500 A aluminium BUS BAR NOS. SET 1 NOS
21 | Sub LT panels inside the Receiving substation: Supplying, Erection, Testing and Commissioning of 440 V extensible type Panel Board suitable for indoor installation for use on 440/500 KV earthed system having a symmertrical breaking capacity of 25KA. The panel shall along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | each | 5 |  |  | 0 | 0
INCOMING
MCCB 100 A 415/500 volts, 4 pole 1 no
MCCB 200 A 415/500 volts, 4 pole 1 no
CONTROL VOLTAGE: 230VAC
CRCA MS Sheet 2 Nos.
METERING & INDICATION
CAST RESIN CT’S OF RATIO 500/5A 2 NO
CAST RESIN PT’S 2 NO
DIGITAL AMMETER WITH PHASE SELECTOR SWITCH
DIGITAL VOLTMETER WITH PHASE SELECTOR SWITCH
2 SET OF OF PHASE INDICATING LAMP WITH CONTROL MCB
RELAY SET OF AUXILARY, CONTROL MCB WITH SUITABLE QUANTITY AND RATING 2 SET
BUSBAR
20x5 mm ALLUMIMIUM BUSBAR (TPN) 100 AMP 1 NO.
30x5 mm ALLUMIMIUM BUSBAR (TPN) 200 AMP 1 NO.
OUTGOING
BUSBAR
20x5 mm ALLUMIMIUM BUSBAR (TPN) 100 AMP 2NO.
30x5 mm ALLUMIMIUM BUSBAR (TPN) 200 AMP 2 NO.
22 | LIFT Panel | Each | 1 |  |  | 0
INCOMING
MCCB 200 A 415/500 volts, 4 pole 1 no
CONTROL VOLTAGE: 230VAC
CRCA MS Sheet 2 Nos.
METERING & INDICATION
CAST RESIN CT’S OF RATIO 500/5A 1 NO
CAST RESIN PT’S 1 NO
| DIGITAL AMMETER WITH PHASE SELECTOR SWITCH | [5 empty] | 0
DIGITAL VOLTMETER WITH PHASE SELECTOR SWITCH
1 SET OF OF PHASE INDICATING LAMP WITH CONTROL MCB
PROTECTIVE RELAYS
BUSBAR
30x5 mm ALLUMIMIUM BUSBAR (TPN) 200 AMP 1 NO.
OUTGOING
BUSBAR
30x5 mm ALLUMIMIUM BUSBAR (TPN) 200 AMP 1 NO.
CABLE TRAYS & ROUTE MARKER
23 | Supplying and installing following size powder coated, perforated M.S. cable trays with perforation not more than 17.5% rigidly suspended from the ceiling with M.S. suspenders at a distance not more than 2.5 metre and near every junction/ joint etc complete as required.
a | 300 mm width X 50 mm depth X 1.6 mm thickness | mtr | 720 |  |  | 0
b | 600 mm width X62.5 mm depth X 2.0 mm thickness | mtr | 60 |  |  | 0
c | 900 mm width X62.5 mm depth X 2.0 mm thickness | mtr | 50 |  |  | 0
24 | Supplying and fixing of following sizes powder coated, perforated, M.S. cable trays bends (horizontal) turning at 900 in same plane with perforation not more than 17.5% rigidly jointed with cable tray etc. complete as required.
a | 300 mm width X 50 mm depth X 1.6 mm thick | Each | 25 |  |  | 0
b | 600 mm width X 62.5 mm depth X 2 mm thick | Each | 5 |  |  | 0
25 | Supplying and fixing of following sizes vertical, powder coated, perforated, M.S. cable trays bends (vertical) turning at 900 in another plane with perforation not more than 17.5% rigidly jointed with cable tray etc. complete as required.
a | 300 mm widthX50 mm depthX1.6 mm thick | Each | 60 |  |  | 0
b | 600 mm widthX62.5 mm depthX2 mm thick | Each | 4 |  |  | 0
c | 900 mm widthX62.5 mm depthX2 mm thick | Each | 5 |  |  | 0
26 | Supplying and fixing cable route marker with 10 cm X 10 cm X 5 mm thick G.I. plate with inscription there on, bolted /welded to 35 mm X 35 mm X 6 mm angle iron, 60 cm long and fixing the same in ground as required. | Each | 10 |  |  | 0
MAIN SWITCHES, MCCB'S, MCB'S & MCB DB'S
27 | Supplying and fixing on surface/ recess vertical type following way, 415 volts TPN, MCB distribution board of sheet steel phosphatized and powder painted with 200 amps tinned copper busbar, common neutral link, earth bar, din bar, detachable gland/knock out plate, including interconnections, earthing etc. as required (But without MCB/RCCB/Isolator)
a | 4 way (4 + 18), Double door | Each | 8 |  |  | 0
b | 8 way (4 + 24), Double door | Each | 52 |  |  | 0
c | 6 way (4 + 36), Double door | Each | 26 |  |  | 0
28 | Supplying and fixing SP MCB, 240 volts, 'B' series, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 6 amps to 32 amps | Each | 596 |  |  | 0
29 | Supplying and fixing SP MCB, 240 volts, 'C' series, suitable for inductive/ motor in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 6 amps to 32 amps | Each | 200 |  |  | 0
30 | Supplying and fixing TP&N MCB, 440 volts, 'B' series, suitable for lighting and other loads in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 6 amps to 32 amps | Each | 33 |  |  | 0
b | 40 amps | Each | 28 |  |  | 0
31 | Supplying and fixing TP&N MCB, 440 volts, 'C' series, suitable for inductive/ motor load in the existing MCB DB complete with connections, testing and commissioning etc. as required.
a | 40 amps | Each | 4 |  |  | 0
b | 63 amps | Each | 26 |  |  | 0
32 | Supplying and fixing following rating, four pole, (three phase and neutral), 415 volts, residual curent circuit breaker (RCCB), having a sensitivity current up to 300 milliamperes in the existing MCB DB complete with connections, testing and commisssiong etc as required.
a | 63 amps | Each | 2 |  |  | 0
33 | Supplying and fixing single pole blanking plate in the existing MCB DB complete etc. as required. | Each | 100 |  |  | 0
34 | Supplying and fixing 2 pole and earth, 240 volts, industrial type, socket outlet, enclosed metal plug top along with SP MCB in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required.
a | 32 Amp with "C" series SP MCB | Each | 5 |  |  | 0
35 | Supplying and fixing TPN and earth, 440 volts, industrial type, socket outlet, enclosed metal plug top along with SP MCB in sheet steel enclosure, on surface or in recess, with chained metal cover for the socket outlet and complete with connections, testing and commissioning etc. as required.
a | 32 Amp with "C" series SP MCB | Each | 2 |  |  | 0
WIRING IN PVC CONDUIT (POINT WIRING)
36 | Wiring for light/ fan/ exhaust fan/ call bell point with 1.5 sqmm FR PVC insulated stranded copper conductor single core cable in concealed PVC conduit, with 5 amp modular switch, modular base and cover plate, suitable size G.I. box and earthing the point with same size cable as required.
a | Short Point | Point | 157 |  |  | 0
b | Medium Point | Point | 1045 |  |  | 0
c | Long Point | Point | 716 |  |  | 0
37 | Wiring for light/ fan/ exhaust fan/ call bell point with 1.5 sqmm FR PVC insulated stranded copper conductor single core cable in surface PVC conduit, with 5 amp modular switch, modular base and cover plate, suitable size G.I. box and earthing the point with same size cable as required.
a | Medium Point | Point | 5 |  |  | 0
b | Long Point | Point | 40 |  |  | 0
38 | Wiring for twin control light point with 1.5 sqmm FR PVC insulated stranded copper conductor single core cable in concealed PVC conduit, with 5 amp modular switch, modular base and cover plate, suitable size G.I. box and earthing the point with same size cable as required. | Point | 72 |  |  | 0
39 | Extra for providing and fixing light plug point on board in concealed PVC conduit point wiring with modular type 3 pin 5 amp socket outlet and 5 amp switch including cost of base and cover plat and G.I. box etc. as required | Point | 250 |  |  | 0
40 | Wiring for power plug point with 2x4 sq mm FR PVC insulated stranded copper conductor cable in concealed PVC conduit along with modular type 16 Amp switch and 6 pin 16 amps socket outlet with modular base and cover plate, suitable size G.I. box, earthing the switch box and socket outlet with same size cable etc. as required.
a | Short Point | Point | 139 |  |  | 0
b | Medium Point | Point | 294 |  |  | 0
c | Long Point | Point | 51 |  |  | 0
d | Extra Long Point I | Point | 10 |  |  | 0
41 | Wiring for circuit/ sub main wiring along with earth wire with the following sizes of FR PVC insulated copper conductor, single core cable in concealed PVC conduit as required.
a | 3 X 2.5 sq. mm in 20mm conduit | mtr | 7575 |  |  | 0
b | 3 X4 sq. mm in 25 mm conduit | mtr | 4500 |  |  | 0
c | 4 X 25 sq. mm + 2 x 16 sq mm in 50mm conduit | mtr | 1250 |  |  | 0
42 | Supplying and fixing fo following sizes PVC conduit along with accessoreis in concealed complete as required.
a | 20 mm | mtr | 1200 |  |  | 0
b | 25 mm | mtr | 800 |  |  | 0
c | 32 mm | mtr | 260 |  |  | 0
d | 50 mm | mtr | 240 |  |  | 0
SWITCHES & ACCESSORIES
43 | Supplying and fixing following modular switch, socket, other accessories on the existing modular plate & switch box including connections but excluding modular plate etc. as required.
a | Telephone socket outlet | Each | 512 |  |  | 0
b | T.V. antenna socket outlet | Each | 40 |  |  | 0
c | Computer Outlet Jack | Each | 560 |  |  | 0
d | 3 pin 5/6 amp socket outlet | Each | 494 |  |  | 0
44 | Providing and fixing composite unit for computer points having modular type 1 No 6 pin 16 amp socket outlet, 1 No 16 amp switch, 3 Nos 3 pin 6 amp socket outlets, 3 Nos 6 amp switches, suitable G.I. box, base and cover plates, earthing the sockets and switch box including etc. as required. | Each | 40 |  |  | 0
WIRING IN EXISTING CONCEALED / SURFACE STEEL / PVC CONDUIT
45 | Supplying and drawing following pair 0.5 sq mm FR PVC insulated copper conductor, unarmored telephone cable in the existing surface/ concealed steel/ PVC conduit as required.
a | 4 Pair | mtr | 4500 |  |  | 0
46 | Supplying and drawing following co-axial TV cable PE insulated, shielded with fine tinned copper braid and protected with PVC sheath in the existing surface/ concealed steel/ PVC conduit as required.
a | RG-8 grade, 0.7 mm solid copper conductor | mtr | 2200 |  |  | 0
FANS, LUMINARIES AND LAMPS
47 | Supplying, installation, testing and commissioning of following sizes ceiling fan with resistance type regulator, including wiring the down rods of standard length up to 30 cm with 1.5 sq. mm FR PVC insulated, copper conductor, single core cable, earthing etc. complete as required.
a | 1400 mm sweep | Each | 368 |  |  | 0
48 | Supplying and fixing following sizes of down rod of 15/20mm dia M.S. pipe of thickness 1.6mm to ceiling fan including painting with matching colour etc. as required.
a | 90 cm long | Each | 368 |  |  | 0
49 | Providing and fixing phenolic laminated sheet cover of 180 mm dia 3 mm thick on the fan box etc. as required. | Each | 368 |  |  | 0
50 | Supplying and fixing modular stepped type electronic fan regulator (two module size) moving all rounds on the existing modular plate and switch box including connections but excluding modular plate etc. as required. | Each | 368 |  |  | 0
51 | Supplying, installation, testing and commissioning of following sizes fancy exhaust fan having built in lovers in existing opening in wall including earthing etc. complete as required.
a | 300 mm sweep | Each | 63 |  |  | 0
52 | Supplying and fixing modular blanking plate on the existing modular plate & switch box excluding modular plate as required. | Each | 350 |  |  | 0
53 | Supplying, installation, testing and commissioning of following surface/concealed type fluorescent fitting (luminaries) complete with copper ballast, glow type starter but without fluorescent lamp, on celing/ wall surface, earthing the fitting etc. as required.
a | 4'x40 W single patti type | Each | 37 |  |  | 0
54 | Supplying, installation, testing and commissioning of following T-5 fluorescent fitting (luminaries) coplete with electronic ballast but without fluorescent lamp, on celing/ wall surface, earthing the fitting etc. as required.
a | single box type with decorative end caps | Each | 458 |  |  | 0
b | Single mirror optic surface mounting type | Each | 114 |  |  | 0
c | Double mirror optics recessed mounting type | Each | 42 |  |  | 0
55 | Supplying, fixing, testing and commissioning of following 230/250 volts fluorescent lamp (tube) in existing lighting luminaries as required. | [6 empty] | 110
a | 4' x 36/40 Watt | Each | 37 |  |  | 0 |  | 103
b | 4'x28 Watt | Each | 656 |  |  | 0 |  | 92
56 | Supplying, installation, testing and commissioning of following mirror optics concealed type CFL fitting (luminaries) complete with copper ballast, but without CFL lamp, in false ceiling, earthing the fitting etc. as required.
a | 2 x 18 W | Each | 912 |  |  | 0
57 | Supplying, fixing, testing and commissioning of following CFL without ballast in existing CFL lighting luminaries as required. | [6 empty] | 91
a | 18 W | Each | 1824 |  |  | 0 |  | 91
58 | Supplying and fixing 3 pin, 5 amp ceiling rose on the existing junction box/wooden block including connection etc as required. | each | 262 |  |  | 0
59 | Supplying and fixing polycarbonate batten/ angle holder including connection etc. as required. | each | 491 |  |  | 0 |  | 4
60 | Supplying , fixing, testing and commissioning of following CFL (built in choke type) in existing lighting luminaries as required.
a | 20 W | Each | 491 |  |  | 0
61 | Supplying, installation, testing and commissioning of following 230/250 volts metal halide wide beam flood light luminaries with weather proof geat box, igniter, capacitor with IP 65 protection on wall surface/building parapet/pole bracket complete but without lamp as required
a | 1x70W | Each | 5 |  |  | 0
62 | Supplying, installation, testing and commissioning of following 230/250 volts metal halide wide beam flood light luminaries with weather proof geat box, igniter, capacitor with IP 65 protection on wall surface/building parapet/pole bracket complete but without lamp as required
a | 70 W double ended | Each | 5 |  |  | 0
POLE AND POLE ERECTION
63 | Supply of hot dipped galvanized (in single dip to average 70 micron) octoganal pole made of 3mm thick steel plate having base plate 200x200x12mm, window and flush cover with locking arrangement at suitable height from base for cable termination block, pole suitably reinforced with welded steel section at window cut section to make the strength of pole unaffected, including template and anchor plate 240x240x3mm with 4 nos 450mm long, 16mm dia foundation bolts bolts (EN8 grade).
a | 5 metre high, minimum dia 129mm at bottom and 75mm at top | Each | 23 |  |  | 0
64 | Supply and fixing following street light pole bracket on existing pole made out of 50 mm dia MS "B" class pipe welded to 300 mm long MS pole canopy of suitable dia at a angle of 102.50 including having MS triangular stiffner of size 150 X 50 X 5 mm thick, making arrangement for tightening the bracket with pole by providing suitable size heavy duty nuts and bolts in canopy, painting with one coat of approved steel primer etc. as required.
a | Single Over Hang 0.75 metre Long | Each | 23 |  |  | 0
65 | Erection of GI octogonal pole on existing cement concrete foundation having grouted bolts and nuts, aligning in true vertical position as required.
a | 5 metre high | Each | 23 |  |  | 0
66 | Designing and providing suitable RCC foundation for 3m to 12 metre high GI octagonal pole including steel reinforcement (minimum 90kg per cum), form work, embeding 2 nos 50mm dia PVC pipe for cable entry in each foundation, excavation disposal of surplus soil and curing etc. as required. (size: 400 x 400 x 1200mm) | cum | 6 |  |  | 0
67 | Supply of 45W IP65 LED streetlight Luminaire complete with pressure die cast aluminum housing. The fixture shall be designed so as to have lumen maintenance of at least 70% at the end of 50,000 hours. Power Factor of the electronic driver should be at least 0.95 with THD<10% and efficiency of the luminaire to be more than 85%. Effective lumen package of greater than 3600 Lumens, LED colour temperature should be 5500 K and CRI greater than 75. Imapct Resistance Level should be IK05. | each | 23 |  |  | 0 | 0
68 | Supplying and drawing following sizes of FR PVC insulated copper conductor, single core cable in the existing surface/ concealed, steel/ PVC conduit/ PVC casing caping as required.
a | 3x1.5 sq mm | mtr | 150 |  |  | 0
69 | Earthing with GI earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as required. | Nos. | 3 |  |  | 0
70 | Supplying and laying 6 SWG G.I. Wire at 0.50 meter below ground level for conductor earth electrode, including soldering, excavation and refilling the trench etc. as required. | mtr | 450 |  |  | 0
71 | Supplying andlaying following sizes one number PVC insulated, PVC sheathed, steel armoured, aluminium conductor power cable of 1.1 KV grade direct in ground including excavation, sand cushioning, protective covering and refilling the trench etc as required
a | 4 x 10 sq mm. | mtr | 450 |  |  | 0
72 | Supplying and making end termination with brass compression gland and aluminum lugs for following size armoured aluminum conductor power cable of 1.1 KV grade as required.
a | 4x10 sq mm | Each | 44 |  |  | 0
73 | Design, Fabrication, Supply, Erection, Testing and commisioning of Powder coated, Weather Proof Double door type Feeder pillar fabricated out of 14 guage CRCA sheet steel in cubical, free standing, dust and vermin proof, with reinforcement of suitable size angle iron, channel, T -iron or flats as required. Feeder pillar shall be treated with all anti-corrosive process before painting as per specification. Feeder Pillar shall be suitable for 415V, 3-Phase, Four wire, 50 Hz supply complete with earth bus and lifting hooks as required in case of large panels.Approval shall be taken for each panel before fabrication. (All hardwares like nuts and bolts used shall be Galvanized and Zinc passivated) | Set | 1 |  |  | 0
INCOMER
1No. 80A FP MCCB(35 KA)
1No. 100A FP Contactor, AOM switch & Timers for 24 Hrs. setting
Metering & Indication
1 set of phase indicating lamps
BUS-BAR
1 Set of 100A TPN Aluminium Bus Bar with colour coded PVC Sleeves
OUTGOINGS
10 Nos. 20A FP MCB
74 | Supply, Installation, wiring, connection, testing and commissioning of flood light conforming to the technical specifications and drawings forming part of this document. The work for each light point comprises of: | Nos. | 2 |  |  | 0
| Supplying, Storing, Handling and Mounting the flood light fixture with one no. 400 watts HPI-T lamp on brick pedestal, Connecting the fixture by using suitable size PVC flexible copper wires of colour green, red and black to the junction box.(The civil construction materials are the part of the supply against this assignment) | [5 empty] | 0
Testing the connections and completing the installation
EARTHING
75 | Earthing with G.I. earth pipe 4.5 mtr long, 40 mm dia including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe etc. with charcoal and salt as required. | set | 5 |  |  | 0
76 | Earthing with copper earth plate 600 mm X 600 mm X 3 mm thick including accessories, and providing masonry enclosure with cover plate having locking arrangement and watering pipe, with charcoal and salt as required. | Nos. | 6 |  |  | 0
77 | Providing and laying earth connection from earth electrode with 4.00 mm dia copper wire in 15 mm dia G.I. pipe from earth electrode at 0.5 meter depth below ground level including excavation and refilling the trench etc as required. | meter | 50 |  |  | 0
78 | providing and fixing 4.00 mm dia copper wire on surface or in recess for loop earthing along with existing surface/ concealed conduit/ submain wiring/ cable as required. | meter | 750 |  |  | 0
SUB STATION SAFETY EQUIPMENT
79 | Supply and fixing glass framed standard shock treatment chart in two different languages in A2 size. | Job | 2 |  |  | 0 | 0
80 | Supply and fixing of flame retardant electrical insulation mat of 3.0 mm thick to withstand upto 33 kV conforming to IS: 15652:2006 with upto date amendments and having minimum width 1000mm (+ 20mm). The sufficient of adhesive/ compound shall be supplied to fix the insulation mat on the front/ rear side of electrical installation. Mat shall be ISI marked. The mat shall be welded by hot gas welding with filler matrial method by making V grove cut at joints with suitable welding cord of insulating material of matching colour to provide a seamless jointed surface as per IS: 8002. | RM | 10 |  |  | 0 | 0
81 | Supply and fixing single line diagram, schematic diagrams etc. of A1 size on suitable Aluminium sheet including lamination etc. as required complete on wall. | Job | 1 |  |  | 0 | 0
82 | Supply & fixing following danger notice plate made of mild steel sheet of at least 2mm thick & vitreous enamelled white on both sides and with inscription in signal red colour on front side as required.
a | Danger board for 33KV size 250mm x 200mm. | Each | 2 |  |  | 0 | 0
b | Danger board for 433V size 200mm x 150mm. | Each | 5 |  |  | 0 | 0
c | Caution board printed in signal red "Man on Line", size 200mm x 150mm. | Each | 2 |  |  | 0 | 0
d | Caution board printed in signal red "Don’t switch on", size 200mm x 150mm. | Each | 2 |  |  | 0 | 0
83 | Supply and fixing G.I. Fire Buckets 13 litre capacity painted in post office red colour and written with white paint 'FIRE', filled with Dry Sand and suitable hanging arrangement on wall hook made out of 13 mm dia MS rod & conforming IS: 2546 - 1974. | Each | 6 |  |  | 0 | 0
84 | Supply of First Aid Box containing material as prescribed by St. John Ambulance brigade OR Indian Red Cross conforming to IS: 2217-1963. | Each | 4 |  |  | 0 | 0
85 | Supply of insulating rubber hand gloves, 33KV grade | Sets | 2 |  |  | 0 | 0
LIFT WORK
86 | Suppy, installation, testing & commissitioning and putting into operation and final testing of automatic lift complete with all standard equipments, accessories and control equipments as per manufacturer's design and as per CPWD specification (Part III LIFTS) 1981 and fulfilling following requirments on turn key basis. | Nos. | 1 |  |  | 0 | 0
A. Type: Passenger lift
B. Load: 8 passenger/ 544 Kg
C. Speed: 1.0 metre per second
D. Contol: AC2
E. Operation: Microprosser based simplex collective selective with/ without lift attendent
F. Total rise: About 15 mtrs
G. Landings: 6 All on same side
I. Signals: Digital car position indicator, car travel direction
indicator in car & at all landings
J. Lift shaft size: About 1900 mm width X 1800 mm depth, finished
with plaster
K. Lift car size: About 1700 mm width X 1600 mm depth
L. Car entrance: Clear opening 800 mm wide X 2000 mm high
protected with car door
M. Landing entrance: Clear opening 800 mm wide X 2000 mm
high protected with landing door
N. Car door: Stainless steel two pannel centre opening flush type
O. Landing door: Mild steel two pannel centre opening flush type
P. Door operation: Automatic electric power operated door with
infra red protection
Q. Car interior: Stainless steel pannel with hair line finish on all
sides
R. Car floor: Hard wood covered with PVC/ marblex tiles
S. Car ceiling & lighting: Fluorscent lighting concealed by
suspended false ceiling with plain acrylic diffuser. The frame of
T. Car ventilation : Pressure fan with anodised aluminium grill
U. Emergency lighting in car: Battery operated Emergency lighting
in the lift car
V. Intercom system: Battery operated Intercom system in lift car,
machine room and control room
W. Emergency alarm: Battery operated alarm bell system in lift car
& contol room
X. Position of machine room: Directly above the lift shaft
Y. Electric power supply: AC 415 Volts 3 phase 50 Hz terminated
in machine room
Z. Fire man switch: Fire man switch at main landing termanal
87 | Suppy, installation, testing & commissitioning and putting into operation and final testing of automatic lift complete with all standard equipments, accessories and control equipments as per manufacturer's design and as per CPWD specification (Part III LIFTS) 1981 and fulfilling following requirments on turn key basis. | Nos. | 1 |  |  | 0 | 0
A. Type: Passenger lift
B. Load: 8 passenger/ 544 Kg
C. Speed: 1.0 metre per second
D. Contol: AC2
E. Operation: Microprosser based simplex collective selective with/ without lift attendent
F. Total rise: About 15 mtrs
G. Landings: 6 All on same side
I. Signals: Digital car position indicator, car travel direction
indicator in car & at all landings
J. Lift shaft size: About 2100 mm width X 1900 mm depth, finished
with plaster
K. Lift car size: About 1900 mm width X 1700 mm depth
L. Car entrance: Clear opening 800 mm wide X 2000 mm high
protected with car door
M. Landing entrance: Clear opening 800 mm wide X 2000 mm
high protected with landing door
N. Car door: Stainless steel two pannel centre opening flush type
O. Landing door: Mild steel two pannel centre opening flush type
P. Door operation: Automatic electric power operated door with
infra red protection
Q. Car interior: Stainless steel pannel with hair line finish on all
sides
R. Car floor: Hard wood covered with PVC/ marblex tiles
S. Car ceiling & lighting: Fluorscent lighting concealed by
suspended false ceiling with plain acrylic diffuser. The frame of
T. Car ventilation : Pressure fan with anodised aluminium grill
U. Emergency lighting in car: Battery operated Emergency lighting
in the lift car
V. Intercom system: Battery operated Intercom system in lift car,
machine room and control room
W. Emergency alarm: Battery operated alarm bell system in lift car
& contol room
X. Position of machine room: Directly above the lift shaft
Y. Electric power supply: AC 415 Volts 3 phase 50 Hz terminated
in machine room
Z. Fire man switch: Fire man switch at main landing termanal
| SUB TOTAL OF PART C : ELECTRICAL WORKS |  |  |  |  | 0

## BOQ (D -HVAC)
BILL OF QUANTITY: HVAC WORKS : PART-D
S.No. | Description of Items | Unit | QTY. | Rate in Figure (in INR) | Rate in words (in INR) | Amount (in INR)
AC UNITS
1 | Supplying and fixing of approved make split type Air Conditioner unit and fixing cooling unit on wall at desired location and condensing unit on out side wall/ ceiling/ floor at desired location having standard length of/ upto 3 metre of copper piping with insulation and drainage pipe upto 1.5 metre length, necessary wiring including providing and fixing necessary good quality powder coated MS frame etc complete as required.
a | 3.0 TR Cassettee SPLIT type capacity 9000kcal/hr. | Nos | 30 |  |  | 0
Refrigerant Piping
2 | Supply, Installation, testing and commissioning of Interconnecting refrigerant pipe work with (19 mm/13mm thick) closed cell elastomeric nitrile rubber tubular insulation between each set of indoor & outdoor units as per specifications, all piping inside the room shall be properly supported with MS hanger and all external piping shall run in covered cable tray.
a | 19.1 mm O.D.(insulation : 13 mm) | Rm | 150 |  |  | 0
b | 15.9 mm O.D.(insulation : 13 mm) | Rm | 160 |  |  | 0
c | 12.7 mm O.D.(insulation : 13 mm) | Rm | 150 |  |  | 0
d | 6.4 mm O.D.(insulation : 13 mm) | Rm | 160 |  |  | 0
3 | Supply, Installation, testing and commissioning of PPRC piping complete with fittings, supports as per specifications.
a | 25 mm Dia | Rmt | 190 |  |  | 0
4 | MS Angle support for Casette Indoor units | Set | 30 |  |  | 0
5 | MS Stand for outdoor unit
a | For Split and Cassete AC | Nos | 30 |  |  | 0
6 | Gas top -up & Nitrogen testing | One job | 1 |  |  | 0
7 | Supplying and drawing following sizes of PVC insulated copper conductor, electrical cable in the existing surface/concealed, steel/ PVC conduit/ PVC casing caping as required.
a | 3 x 2.5 sq. mm | Rm | 400 |  |  | 0
AIR COOLING
8 | Supply and Installation GI duct work, factory fabricated spotless GP sheets, GI flanges & cleats, gaskets, GI nuts and bolts and threaded rods. All ducts pieces shall be fully fabricated in factory and joined together at site. Duct fabrication and duct supports shall be as per IS-655.
a | 24 G | Sq.M | 530 |  |  | 0
b | 22 G | Sq.M | 1576 |  |  | 0
c | 20 G | Sq.M | 942 |  |  | 0
9 | Supply and fixing of Powder coated Cont. Aluminium supply air Grill. Grills shall have flange on all four sides. | Sq.M | 127 |  |  | 0
10 | Supply and fixing of 40Ø GI B class drain piping from Air Washer drain point and Monobloc pump up to nearest drain sump complete with masonry pipe supports with Pcc uthalas.
a | 40 mm | Rm | 154 |  |  | 0
11 | Supplying, installation, testing and commissioning of following sizes heavy duty (continuous running) exhaust fan in existing opening in wall including earthing etc. complete as required.
a | 450 mm sweep | Nos | 20 |  |  | 0
12 | Supply and Application of thermal insulation of ducting with approved sample of closed cell Elastomeric Nitrile rubber insulation, as per specifications.
a | 6 mm thick with aluminum foil | SqM | 3130 |  |  | 0
| SUB TOTAL OF PART D : HVAC WORKS |  |  |  |  | 0

## BOQ ( E- WS & PLUMBING)
BILL OF QUANTITY : PUBLIC HEALTH ENGINEERING : PART-E
S.No. | Description of Items | Unit | QTY. | Rate in Figure (in INR) | Rate in words (in INR) | Amount (in INR)
SANITARY FIXTURES & CP FITTINGS
1 | Providing and fixing water closet squatting pan (Indian type W.C. pan), 100mm sand cast Iron P or S trap, 10 litre low level P.V.C. flushing cistern (same colour) conforming to IS : 7231, with flush bend and other fittings and fixtures complete including cutting and making good the walls and floors wherever required :
a | White Orissa pattern W.C. pan of size 580x440 mm | Each | 30 |  |  | 0
2 | Providing and fixing vitreous china water closet (European type W.C. pan) with white ISI marked plastic seat and lid, 10 litre low level white P.V.C. flushing cistern (same colour), conforming to IS : 7231, with all fittings and fixtures complete including cutting and making good the walls and floors wherever required :
a | White wall hung type | Each | 20 |  |  | 0
b | Coloured wall hung type | Each | 11 |  |  | 0
3 | Providing and fixing 15 mm nominal bore uplasticised PVC connection pipe with C.P brass nuts collar and PVC bush of approved quality and colour:
a | 30 CM length | Each | 31 |  |  | 0
b | 45 CM length | Each | 30 |  |  | 0
4 | Providing and fixing white vitreous china urinal basin with waste fitting as per IS : 2556, and other couplings in C.P. brass complete:
a | Flat back half stall urinal of size 580x380x350mm | Each | 30 |  |  | 0
5 | Providing and fixing Sensor type Concealed Type Flushing Valve for Urinal Complete Set with Installation Box with Control Cock including connecting spreader for individual urinals complete in all respects including cutting and making good the walls where ever required. | Each | 30 |  |  | 0 | 0
6 | Providing and fixing vitreous china wash basin with C.I. brackets, 32 mm C.P. brass waste of standard pattern, including painting of brackets, cutting and making good the walls wherever required :
a | White Size 630x450 mm | Each | 31 |  |  | 0
b | White Oval or round size 560x410mm. | Each | 33 |  |  | 0
7 | Providing and fixing Stainless Steel A ISI 304 (18/8) kitchen sink without drain board as per IS 13983 with C.I. brackets and stainless steel plug 40 mm including painting of fittings and brackets, cutting and making good the walls wherever required :
a | 610x510 mm bowl depth 200 mm. | Each | 2 |  |  | 0
8 | Providing and fixing flexible P.V.C. waste pipe for sink or wash basin including P.V.C. waste fittings complete.
a | 32 mm dia | Each | 94 |  |  | 0
b | 40 mm dia | Each | 2 |  |  | 0
9 | Providing and fixing cast iron grating for gully trap.
a | 150x150mm square | Each | 139 |  |  | 0
10 | Providing and fixing 600x450 mm beveled edge 4mm mirror of superior glass (of approved quality) complete with 6 mm thick hard board ground fixed to wooden cleats with C.P. brass screws and washers complete. | Each | 32 |  |  | 0
11 | Providing and fixing mirror of superior glass (of approved quality) and of required shape and size with plastic moulded frame of approved make and shade with 6 mm thick hard board backing :
a | 5mm thick mirror | each | 31 |  |  | 0
12 | Providing and fixing vitreous china Division Plate 700 x 340 x 120mm with expandable anchor fasteners with C.P. brass bolts and washers complete, including cutting and making good the walls where required to the satisfaction of Engineer in charge. | Each | 20 |  |  | 0 | 0
13 | Providing and fixing CP brass hand shower (health faucets) with 8 mm dia 1meter long flexible tube and wall hook with all fittings and fixtures complete inlcuding cutting and making good the walls and floors wherever required: | Each | 31 |  |  | 0 | 0
14 | Providing and fixing two way bib cock including nessacary cutting and making good. | each | 31 |  |  | 0 | 0
15 | Providing and fixing Pillar cock including nessacary cutting and making good. | Each | 32 |  |  | 0 | 0
16 | Providing and Fixing C.P. Brass Pillar Cock Pressmatic type (Autoclosing System) of 15 mm dia & including necessary cutting and making good ) (for handwash and wash basin) | Each | 31 |  |  | 0 | 0
SOIL WASTE, VENT & RAIN WATER PIPES
17 | Providing and fixing uPVC pipes ( confirming to IS 4985-2000 ) fixing with as recommended by the manufacturer, necessary fixing arrangement including cutting chase or holes in walls / floors and making good the same complete as per specification.
a | 75 mm dia pipe ( 6 Kg/Cm2 Pressue Rating ) | Metre | 243 |  |  | 0 | 0
b | 110 mm dia pipe ( 6 Kg/Cm2 Pressue Rating ) | Metre | 470.5 |  |  | 0 | 0
18 | Providing and fixing on wall face UV stabilized Unplasticised -PVC moulded fittings/ accessories having 3.2mm wall thickness for Rigid PVC pipes conforming to IS : 13592 (heavy) jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.
a | Single tee with door
i | 110x110x110 mm | Each | 33 |  |  | 0
b | Plain bend
i | 110 mm bend | Each | 51 |  |  | 0
c | Vent covel
i | 110 mm | Each | 22 |  |  | 0
d | P trap 110mmx110mm long | each | 80 |  |  | 0
e | Multi floor trap 110 | each | 139 |  |  | 0
f | Plain reducing Tee 110x75mm | each | 41 |  |  | 0
19 | Providing and fixing on wall face UV stabilized Unplasticised -PVC moulded fittings/ accessories having 3.2mm wall thickness for Rigid PVC pipes conforming to IS : 13592 (heavy) jointing with seal ring conforming to IS : 5382 leaving 10 mm gap for thermal expansion.
a | Double Y bend 110 dia | Each | 8 |  |  | 0 | 0
b | Socket plug
i | 75 mm Dia | Each | 53 |  |  | 0 | 0
ii | 100 mm Dia | Each | 50 |  |  | 0 | 0
c | Reducer | Each | 12 |  |  | 0 | 0
WATER SUPPLY SYSTEM
20 | Providing and fixing Chlorinated Polyvinyl Chloride (CPVC) pipes in concealed in wall, having thermal stability for hot & cold water supply including all CPVC plain & brass threaded fittings i/c fixing the pipe with clamps at 1.00 m spacing. This includes jointing of pipes & fittings with one step CPVC solvent cement and the cost of cutting chases and making good the same including testing of joints including cutting chases and making good the walls etc complete as per direction of Engineer in Charge.
a | 15 mm nominal outer dia .Pipes. | Metre | 44.25 |  |  | 0
b | 20 mm nominal outer dia .Pipes. | Metre | 31.5 |  |  | 0
c | 25 mm nominal outer dia .Pipes. | Metre | 376.65 |  |  | 0
21 | Providing and laying in trenches/above terrace/inside shaft G.I. pipes medium class complete with G.I. fittings including excavation of trenches, refilling the same and testing of joints complete:
a | 25 mm dia. nominal bore | Metre | 88.5 |  |  | 0
b | 32 mm dia. nominal bore | Metre | 250 |  |  | 0
c | 50 mm dia. nominal bore | Metre | 135 |  |  | 0
d | 65 mm dia. nominal bore | Metre | 45 |  |  | 0
e | 80 mm dia. nominal bore | Metre | 90 |  |  | 0
22 | Making connection of G.I. distribution branch in G.I. main of following sizes by providing and fixing tee, including cutting and threading the pipe etc. complete: (Dia of main line to be measured)
a | 50 mm nominal bore | Each | 11 |  |  | 0
23 | Providing and fixing G.I. Union in G.I. pipe (New work) including cutting and threading the pipe and making long screws etc. complete:
a | 25 mm nominal bore | Each | 30 |  |  | 0
b | 32 mm nominal | Each | 35 |  |  | 0
c | 50mm nominal bore | Each | 10 |  |  | 0
24 | Providing and fixing 15 mm nominal bore C.P. brass fittings of approved make and conforming to IS:8931 including C.P. brass extension if required:
a | Bib cock (450gms) | Each | 30 |  |  | 0
b | Angle valve for basin mixer and geyser points (450gms) | Each | 139 |  |  | 0
c | Bottle trap set with extension pipes | Each | 65 |  |  | 0
d | Toilet paper holder | Each | 31 |  |  | 0
e | Soap dish plate | Each | 52 |  |  | 0
f | Towel rail (600mm long x 20mm dia) | Each | 31 |  |  | 0
25 | Providing and fixing stainless steel drain jali of approved make/quality. | Each | 139 |  |  | 0
26 | Providing and fixing gun metal gate valve with C.I. wheel of approved quality (screwed end):
a | 25 mm nominal bore | Each | 51 |  |  | 0
b | 32 mm nominal bore. | Each | 11 |  |  | 0
c | 50 mm nominal bore | Each | 6 |  |  | 0
27 | Providing and fixing ball valve (brass) of approved quality, High or low pressure, with plastic floats complete :
a | 18 mm nominal bore | Each | 5 |  |  | 0
b | 25 mm nominal bore | Each | 13 |  |  | 0
28 | Providing and fixing gun metal non- return valve (horizontal type) of approved quality (screwed end) :
a | 50 mm nominal bore | Each | 4 |  |  | 0
b | 65 mm nominal bore | Each | 2 |  |  | 0
29 | Providing and fixing gun metal non- return valve (vertical type) of approved quality (screwed end) :
a | 65 mm nominal bore | Each | 1 |  |  | 0
30 | Painting G.I. pipes and fittings with two coats of anti-corrosive bitumastic paint of approved quality:
a | 25 mm diameter pipe | Metre | 88.5 |  |  | 0
b | 65 mm diameter pipe | Metre | 45 |  |  | 0
c | 80 mm diameter pipe | Metre | 90 |  |  | 0
31 | Providing and placing in position C.I. double acting air valve of approved make.
a | 50 mm dia | Each | 2 |  |  | 0
32 | Providing and fixing enclosed type water meter (bulk type) conforming to IS : 2373 and tested by Municipal Board complete with bolts, nuts, rubber insertions etc. (The tail pieces if required will be paid separately) :
a | 80/ 50 mm dia nominal bore | Each | 1 |  |  | 0
33 | Providing and fixing C.I. dirt box strainer for bulk type water meter with nuts, bolts, rubber insertions etc. complete conforming to IS : 2373 :
a | 50/80 mm dia | Each | 1 |  |  | 0
34 | Constructing masonry Chamber 30x30x50 cm, inside with fly ash of 35 kg/ cm² in cement mortar 1:4 (1 cement : 4 coarse sand) for stop cock, with C. I. surface box 100x100 x75 mm (inside) with hinged cover fixed in cement concrete slab 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) necessary excavation foundation concrete 1:5:10 ( 1 cement : 5 fine sand:10 graded stone aggregate 40mm nominal size) and inside plastering with cement mortar 1:3 (1 cement : 3 coarse sand) 12mm thick finished with a floating coat of neat cement complete as per standard design : | Each | 1 |  |  | 0
EXTERNAL SEWERAGE & DRAINAGE SYSTEM
35 | Providing, laying and jointing glazed stoneware pipes grade ‘A’ with stiff mixture of cement mortar in the proportion of 1:1 (1 cement : 1 fine sand) including testing of joints etc. complete :
a | 150 mm diameter | Metre | 44 |  |  | 0
36 | Providing and fixing square-mouth S.W. gully trap grade 'A'’ complete with C.I. grating brick masonry chamber with well burnt modular clay bricks crushing strength not less than 35kg/ cm², water tight C.I. cover with frame of 300 x300 mm size (inside) the weight of cover to be not less than 4.50 kg and frame to be not less than 2.70 kg as per standard design :
a | 150 x 100 mm size P type. | Each | 11 |  |  | 0
37 | Providing and fixing uPVC pipes ( confirming to IS 4985-2000 ) fixing with as recommended by the manufacturer, necessary fixing arrangement including cutting chase or holes in walls / floors and making good the same complete as per specification.
a | 160 mm dia ( 6 Kg/Cm2 Pressue Rating ) | Meter | 135 |  |  | 0 | 0
b | 200 mm dia ( 6 Kg/Cm2 Pressue Rating ) | Meter | 412 |  |  | 0 | 0
c | 250 mm dia ( 6 Kg/Cm2 Pressue Rating ) | Meter | 240 |  |  | 0 | 0
38 | Providing & laying cement concrete 1:5:10 (1cement : 5 coarse sand : 10 graded stone aggregate 40mm nominal size) allround UPVC pipes including bed concrete as per standard design:
a | 200mm dia u.P.V.C. pipe | Metre | 50 |  |  | 0 | 0
b | 250mm dia u.P.V.C. pipe | Metre | 240 |  |  | 0 | 0
39 | Constructing brick masonry manhole with fly ais crushing strength not less than 35kg/ cm² in cement mortar 1:4 ( 1 cement : 4 coarse sand), R.C.C. top slab with 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size), foundation in cement concrete 1:4:8 mix (1 cement : 4 coarse sand : 8 graded stone aggregate 40mm nominal size) inside plastering 12mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished with floating coat of neat cement and making channels in cement concrete 1:2:4 (1 cement : 2 coarse sand : 4 graded stone aggregate 20mm nominal size) finished with a floating coat of neat cement complete as per standard design :
a | Inside size 90x80 cm and 45 cm deep including C.I. cover with frame (light duty) 455x610 mm internal dimensions total weight of cover and frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) : ( Type A ) | Each | 15 |  |  | 0
40 | Extra for depth for manholes
a | Size 90x80 cm | meter | 4 |  |  | 0
41 | Providing orange colour safety foot rest of minimum 6 mm thick plastic encapsulated as per IS : 10910 on 12mm dia steel bar conforming to IS : 1786 having minimum cross section as 23 mmx25mm and over all minimum length 263 mm and width as 165mm with minimum 112 mm space between protruded legs having 2 mm tread on top surface by ribbing or chequering besides necessary and adequate anchoring projections on tail length on 138 mm as per standard drawing and suitable to with stand the bend test and chemical resistance test as per specifications and having manufacture's permanent identification mark to be visible even after fixing, including fixing in manholes with 30x20x15 cm cement concrete block 1:3:6 (1 cement : 3 coarse sand : 6 graded stone aggregate 20 mm nominal size) complete as per design. ( Type D ) | Each | 60 |  |  | 0
42 | Supplying and fixing C.I. cover without frame for SUMP TANK & O.H.T. :
455x610 mm rectangular C.I. cover (light duty) the weight of the cover to be not less than 23 kg.
a | FOR SUMP TANK & O.H.T. | EACH | 10 |  |  | 0
43 | Making connection of drain or sewer line with existing manhole including breaking into and making good the walls, floors with cement concrete 1:2:4 mix (1 cement : 2 coarse sand : 4 graded stone aggregate 20 mm nominal size) cement plastered on both sides with cement mortar 1:3 (1 cement : 3 coarse sand) finished with a floating coat of neat cement and making necessary channels for the drain etc. complete :
a | For pipes 100 to 230 mm diameter | Each | 2 |  |  | 0
44 | Providing and constructing brick masonry chamber for underground C.I. inspection chamber and bends with well burnt modular clay bricks crushing strength not less than 35kg/cm² in cement mortar 1:4 (1 cement : 4 coarse sand) C.I. cover with frame (light duty) 455x610 mm internal dimensions, total weight of cover with frame to be not less than 38 kg (weight of cover 23 kg and weight of frame 15 kg) R.C.C. top slab with 1:2:4 mix (1 cement :2 coarse sand : 4 graded stone aggregate 20 mm nominal size) foundation concrete 1:5:10 (1 cement : 5 fine sand : 10 graded stone aggregate 40 mm nominal size), inside plastering 12 mm thick with cement mortar 1:3 (1 cement : 3 coarse sand) finished smooth with a floating coat of neat cement on walls and bed concrete etc. complete as per standard design :
a | Inside dimensions 500x700 mm and 45 cm deep for pipe line with one or two inlets : | Each | 28 |  |  | 0
45 | Providing and laying non-pressure NP2 class (light duty) RCC pipes with collars jointed with stiff mixture of cement mortar in the proportion of 1:2 (1 cement : 2 find sand) including testing of joints etc. complete.
a | 150mm dia RCC Pipe | meter | 200 |  |  | 0
46 | Providing and laying cement concrete 1:5:10 (1 cement : 5 fine sand: 10 graded stone aggregate 40 mm nominal size) upto haunches of RCC pipes including bed concrete as per specifications.
a | 150mm dia RCC Pipe | Metre | 200 |  |  | 0
RAW WATER, WATER SUPPLY AND ACCESSORIES
Note :
- All pumps to be provided with mechanical
seal, wearing ring and base frame.
- Performance curve should be got approved before placing the order.
- In case impeller need to be trimmed to suite discharge & head, it should be tested for actual RPM of motor supplied along with pump considring the slip in RPM at actual working conditions.
47 | Supply and install test commissioning of horizontal split casing type centrifugal pump set single Phase 230 volts along with the following capacity. | Set | 1 |  |  | 0
Domestic water supply Pump :
| Capacity : 5000Ltrs/hr. | [5 empty] | 0
Head : 25 meter
HP : 1 HP or as required
Two Pumps with Electrical Panel
(one working & one Stand bey
48 | Providing and fixing liquid level controller for pumps including probes, wiring, cable, condiut and making connection to pump pannel complete in all respects and making system functional ( sensor sholud be mercury float type.)
For Domestic & Raw pump U.G.Tank to O.H.Tank :
1 no. Each sensor at low level of UG tank to cut in pump, one no.Each at higher level of O.H.Tank to cut off pump, one noEach for dry running protection
a | Sensor with panel | Each | 1 |  |  | 0 | 0
b | Cable ( 2 core 2.5 mm ) | Meter | 70 |  |  | 0 | 0
c | Conduit | Meter | 70 |  |  | 0 | 0
d | Istallation | Each | 1 |  |  | 0 | 0
49 | Providing & fixing subermissble dewarting pump , open impeller sump pump with vortex impeller 400/440 voltas, 50 cycles, AC supply, 3-phase motor of the following specification and inter locking PLC arrangement with Sump Pump (for Drainage for Pump room ) | Set | 2 |  |  | 0
(a) Discharge : 200 lpm
(b) Head : 6 Metre
| (c) HP : 1 HP/As required. | [5 empty] | 0
(d) Casing : S.S. / C.I.
(e) Impeller & Shaft : S.S. 410
(f) Solid Handling Capacity : 50 mm
(g) Length of water proof cable with
each pump:10 Mtr.
(h) Length of GI lifting chain withEach
pump : 5 Mtr.
(i)2 pumps with panel
| SUB TOTAL OF PART E : PUBLIC HEALTH ENGINEERING WORKS |  |  |  |  | 0 | 0

## BOQ (F-FIRE FIGHTING)
BILL OF QUANTITY: FIRE FIGHTING & DETECTION : PART-F
S. No. | Description of Items | Unit | QTY. | Rate in Figure (in INR) | Rate in words (in INR) | Amount (in INR)
FIRE FIGHTING SYSTEM AND HYDRANT
1 | Providing, laying, testing and commissioning of C class heavy duty MS pipe conforming to IS: 1239 / IS:3589 including MS fittings like elbows, tees, flanges, tapers, nuts, bolts, gaskets etc., in ground including excavation and providing cement concrete blocks as supports, anticorrosive treatment with coaltar / asphaltic tape as per IS:10221, refilling the trench etc. complete of following sizes as required.
a | 25mm dia. | Metre | 1255 |  |  | 0
b | 32mm dia. | Metre | 950 |  |  | 0
c | 40mm dia. | Metre | 188 |  |  | 0
d | 50mm dia. | Metre | 270.5 |  |  | 0
e | 65 mm Dia | Metre | 300 |  |  | 0
f | 80 mm Dia | Metre | 180 |  |  | 0
g | 100mm dia. | Metre | 150 |  |  | 0
h | 150mm dia. | Metre | 225 |  |  | 0
i | 200mm dia | Metre | 15 |  |  | 0
2 | Painting for M.S. pipe with a coat of red oxide primer and two or more coats of synthetic enamel paint of approved colour and Quality to give an even shade including surface preparation.
a | 25mm dia. | Metre | 1255 |  |  | 0
b | 32mm dia. | Metre | 950 |  |  | 0
c | 40mm dia. | Metre | 188 |  |  | 0
d | 50mm dia. | Metre | 270 |  |  | 0
e | 65 mm Dia | Metre | 300 |  |  | 0
f | 80 mm Dia | Metre | 180 |  |  | 0
g | 100mm dia. | Metre | 45 |  |  | 0
h | 150mm dia. | Metre | 120 |  |  | 0
i | 200 mm dia | Meter | 15 |  |  | 0
3 | Providing and applying one coat of 4 mm thick anti rust pipe protection including approved primer as per manufacturers specifications and lap of 25 mm to make an impermeable layer on MS pipes in trenches or on structural/masonary members complete including surface preparation
a | 100 mm dia | Meter | 105 |  |  | 0
b | 150 mm dia | Meter | 105 |  |  | 0
4 | Supplying and fixing Stainless Steel ‐IS:3444 Grade‐1 single headed internal/ external hydrant valve with instantaneous Stainless Steel couplings of 63 mm dia with cast iron wheel ISI marked conforming to IS 5290 (Type ‐ A) with blank cap and chain. | Each | 20 |  |  | 0
5 | Supplying and fixing 63 mm dia, 30 mtr. long (FH‐PY) hose pipe with 63 mm dia Male and Female Stainless Steel‐IS:3444 rade‐1 couplings duly binded with GI wire, rivets etc. conforming to IS 636 (Type ‐A) as required. | Each | 40 |  |  | 0
6 | Supplying and fixing First‐Aid Hose Reel with MS construction spray painted in Post office Red, cinforming to IS 884 with upto date amendments, complete with the following as required. | Set | 18 |  |  | 0
30 m. long 20 mm (nominal internal) dia water hose (rubber / thermoplast )as per IS: 444 marked.
20 mm (nominal internal) dia gun metal globe valve & nozzle.
Drum and brackets for fixing the equipmets on wall.
Connections from riser with 25 mm dia stop valve (gun metal) & M.S. Pipe.
7 | Supplying & fixing 63 mm dia Stainless Steel IS: 3444 Grade‐1 branch pipe with 20 mm (nominal internal diameter) size Gun Metal nozzle conforming to IS 903, suitable for instantaneous connection to interconnect hose pipe coupling as required. | Each | 22 |  |  | 0
8 | Supplying and fixing of hose cabinet of size 900 mm x 600 mm x 500 mm made of 16 gauge MS sheet with 6 mm thick glazed glass doors i/c 'necessary locking arrangement suitable to accommodate external hydrant with butterfly valve, 2 Nos. 15 mtr. long Hose | Each | 4 |  |  | 0
9 | Supplying and fixing of hose cabinet shutter of size 900 mm x 2100 mm x 600, with door frame made of 2 mm thick SS sheet and 40x40x5 Stainless Steel Grade-304 angle with 6 mm thick glazed glass doors i/c 'necessary locking arrangement , as required. | Each | 18 |  |  | 0
10 | Providing, installation, testing and commissioning of non return valve of following sizes confirming to IS: 5312 complete with rubber gasket, GI bolts, nuts, washers etc. as required.
a | 100mm dia | Each | 1 |  |  | 0
b | 150mm dia | Each | 5 |  |  | 0
11 | Supplying, fixing, testing and commissioning of butterfly valve PN 1.6, duly ISI marked complete with Nuts, Bolts, washers, gaskets, conforming to IS 13095 of following sizes as required.
a | 100mm dia | Each | 18 |  |  | 0
b | 150mm dia | Each | 5 |  |  | 0
12 | Providing and fixing brass ball valve (full bore type) with plastic coated lever and screwed female ends tested to 20 Kg/ cm2 of approved quality as specified.
a | 50 mm dia | Each | 18 |  |  | 0
13 | Providing and fixing suction coupling for fire brigade drawl of water from tank with 150 mm dia GI (Medium) pipe and foot valve (Pipe max 8 M long). | Each | 1 |  |  | 0
14 | Providing and fixing M.S. structural work fabricated from standard sections, (MS rounds, angles, channels etc.) including cutting to size,drilling welding including cost of (Hilti) fasteners, clamp in RCC structural members as directed, including two or more coats of synthetic enamel paint over one coat of primer after surface preperation including cutting and making good walls. | KG. | 1100 |  |  | 0
15 | Providing and fixing 150 mm dia C.I. double flanged sluice valves rated to PN 1.6 with C.I. Wheel bolts, nuts,washers 3mm thick insertion rubber gasket including matching flanges table E, complete. | Each | 2 |  |  | 0
16 | Supplying and fixing 4 way fire brigade connection of cast iron body with 4 Nos. Gun metal male instantaneous inlet couplings complete with cap and chain as reqd. for 150mm dia MS pipe connection, conforming to IS 904 as required. | Each | 1 |  |  | 0
17 | Providing and fixing gunmetal single acting air release valve with screwed inlet 25 mm dia. | Each | 7 |  |  | 0
18 | Providing and fixing standard fireman's axe ( tested for 20000 Volts) with heavy insulated rubber handle.( ISI marked) | Each | 18 |  |  | 0
19 | Providing and fixing pressure switch with suitable for 1‐10 Kg/cm2 including electrical connections setting of Cut‐In and cut‐Off pressure complete in all respects. | Each | 6 |  |  | 0
20 | Providing, fixing, testing and commissioning 25mm diameter inspecting and testing assembly with gunmetal isolation valve gunmetal sight glass bypass valve and connected to 50mm drain line. | Each | 18 |  |  | 0
21 | Pendant type with quartzoid bulb, operating temperature at 68˚ C as per specification with rosette plate. | Each | 1217 |  |  | 0
22 | Flow switches suitable for fixing in 50mm to 150mm dia, complete with all accessories to provide indication in annuciator panel. | Each | 18 |  |  | 0
23 | 4 x 2.5 sq.mm cable for annunciations panel of flow switch on the sprinkler line capable of sending impulses to the control room fire pump panel with accessories.
supplying and drawing following sizes of FR PVC insulated copper conductor, single core cable in the existting suface/ concealed, steel/PVC conduit/ PVC casing caping as required
a | 4 X 2.5 sq.mm | Mtr | 350 |  |  | 0
24 | Supply, Install, testing and commissioning of Conventional type sprinklers annunciations panel having a capacity of 12 zone, 80 character display system, catering to max of 22 devices, surface/semi flush mounted, operating temperature between -10 Deg C to +55 Deg C, housing protection with IP43, to work on 220V,50Hz, main supply &24V DC secondary supply etc., complete. The system shall also have network interface module with network software | Each | 1 |  |  | 0
25 | Providing and fixing 150 mm dia installation control valve(alarm valve) complete with all accessories i.e. drain valve, pressure gauge, hydraulic gong etc. excluding associated pipe work. | Set | 1 |  |  | 0
FIRE PUMPS AND ACCESSORIES
DESIEL ENGINE PUMP
26 | Supplying, Installation, Testing and Commissioning of Diesel engine driven main fire pump suitable for automatic operation and consisting of following: complete in all respect as required. | Each | 1 |  |  | 0
Horizontal type, multistage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal to ensure a minimum pressure of 3.5 kg/sq.cm at highest and farthest outlet at specified flow of 2280 lpm at 75 m. head conform
Suitable 95 BHP, 1500 RPM water cooled with radiator, diesel engine conforming to relevant BS& IS standard complete with auto starting mechanism, 12 volts/24 Volts electric starting equipment, Diesel Tank, exhaust pipe extended upto 1 m. outside pump house .
M.S.fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required.
Suitable cement concrete foundation duly plastered with anti vibration pads.
ELECTRIC PUMP
27 | Supplying, Installation, Testing and Commissioning of Electric driven main fire pump suitable. for automatic operation and consisting of following: complete in all respect as required. | Each | 1 |  |  | 0
Horizontal type, multistage, centrifugal, split casing pump of cast iron body & bronze impeller with stainless steel shaft, mechanic.al seal to ensure a minimum pressure of 3.5 kg/sq.cm. at highest and farthest outlet at specified flow of 2280 lpm at 75m head
70 HP Squrrel cage induction motor, TEFC, synchronous speed 1500 RPM, suitable for operation on 415 volts, 3 phase 50 Hz. AC with IP 55 protection for enclosure, horizontal foot mounted type with Class‐'F' insulation, conforming to IS:325.
M.S fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required.
Suitable cement concrete foundation duly plastered with anti vibration pads.
JOCKEY PUMP
28 | Supplying, Installation, Testing and Commissioning of Electric driven pressurisation pump suitable for automatic operation and consisting of following: complete in all respect as required. | Each | 1 |  |  | 0
Horizontal type, singlestage, centrifugal pump of cast iron body and bronze impeller with stainless steel shaft, mechanical seal and flow of 180 lpm at 75 m. head conforming to IS : 1520.
Suitable 10HP Squrrel cage induction motor TEFC type suitable for operation on 415 volts, 3 phase 50 Hz. AC with IP 55 class of protection for enclosure, horizontal foot mounted type with Class‐'F' insulation, conforming to IS : 325.
M.S fabricated Common base plate, coupling, coupling guard, foundation bolts etc. as required.
Suitable cement concrete foundation duly plastered with anti vibration pads.
29 | Supplying and fixing air vessel made of 450 mm dia, 8 mm thick MS sheet,1200 mm. height with air release valve on top and flanged connection to riser, drain arrangement with 25 mm dia Gun metal wheel valve, with required accessories, pressure gauge etc. | Each | 1 |  |  | 0
30 | Supply, installation, testing and commissioning of pressure guage 0 200 PSI ( 0 ‐ 14 Kg ) range, 3/8" BSP bottom entry, 4" dial weather proof with stainless steel internals, siphon tube amd ball valve including fittings, etc. complete as required | Each | 1 |  |  | 0
Terrace Fire Pump
31 | Providing fixing multi stage horizontal centrifugal pump with volute bronze impeller connected to TEFC induction motor suitable for 400/410 Volts, 3 Phase, 50 Cycles, AC Supply with the following specifications: | Each | 1 |  |  | 0
a. Capacity : 450 LPM b. Head : 35 m
c. HP : As required. d. RPM : 2900
e. Mover : Electric Motor driven
f. Material of Construction:
Shaft & Sleeve : S.S. 410
Impeller : Bronze
Bearing : Grease lubricated
Seal - Mechanical seal.
g) Pump foundation as per manufacturer.
Main Fire Pump Panel
32 | Fabricating, supplying, Installtion, testing and commissioning of electrical control panel of cubicle construction, floor mounted type, fabricated out of 2 mm thick CRCA sheet, compartmentalised with hinged locakable doors, dust and vermin proof, cable alley, inter connection, having switchgears and accessories mounting and inernal wiring, earth terminals, numbering etc. complete in all respects, suitable for operation on 415 V, 3 phase, 50 Hz AC supply with enclosure protection class IP 42 as required.
Common panel in Fire Pump House
Incomer
200 Amps TPN, MCCB, 35 KA with Microprocessor based release
Digital Voltmeter ( 0 ‐ 500 volts ) with selector switch
Digital Ammeter ( 0 ‐ 250 Amps ) with selector switch& CTs etc.
Set of 3 phase indicating Lamps LED type with protective fuse.
Set of Al. Bus bar of 250 Amps,
Outgoing
02 Nos. 200 Amp, TPN, 35 KA MCCB with thermal release
02 Nos. 63 Amp, TPN, 25 KA MCCB with thermal release
Main Fire & sprinkler Pump : 2 set per pump
01 nos., 63 Amps TPN, MCCB, 25 KA with thermal magnetic release suitable HP fully automatic star / delta starter with overload protection, current sensing type single phase preventor complete with all accessories and internal wiringrequired for automatic operation, selector switch for local / remote, auto / manual / Off operation.
Jockey Pump
01 nos., 63 Amps TPN, MCCB, 25 KA with thermal magnetic release suitable HP fully automatic DOL starter with overload protection, current sensing type single phase preventor complete with all accessories and internal wiringrequired for automatic operation, selector switch for local / remote, auto / manual / Off operation.
Diesel Engine Control
Control for Diesel Engine comprising :
Auto / manual Selector Switch & 3 attempt starting device, timers and relays as required, push buttons, start / stop in manual mode.
Indication lamp for High / Low Lube Oil pressure, High water Temperature and Engine ON indication.
battery Charger suitable for 12 V / 24 V DC with boost and trickle selector switch, 0 ‐15 V / 0 ‐ 30 V DC volt meter, 0 ‐ 20 A DC Ammeter.
All standard relays and accessories for automatic operation of diesel engine.
| Designing, supply, installation, testing and commissioning of System Controller to control operation of Main Electric Pump, Diesel Pump, and Pressurisation Pump in sequence as per specifications consisting of relays, timers, sensors, annunciation window for fault indication complete as per specifications. | Set | 1 |  |  | 0
Terrace pump panel
33 | Providing and fixing dust & vermin proof cubicle type motor control centre fabricated from powder coated 16 SWG MS sheet for ELECTRICAL PANEL FOR TERRACE PUMP suitable for Terrace fire Pump and automatic/Menual operation complete in all respect as required. | Each | 1 |  |  | 0
Electric panel board comprising of DOL starter auxiliary switch, main in commer, three phase preventer, voltmeter indication lamps, pressure gauge M.C.B.20amp.
Rating including all connections with copper cable etc.
(To start the terrace pumps)
34 | Providing Supplying and insatalling Panel distribution board for fire fighting | Each | 1 |  |  | 0
Incomer
200A TP MCCB with microprocessor based, O/C , S/C & E/F, 36kA 485 Port with release for 400A MCCB, Multifunction meter with port , Digital Voltmeter (0-500V),Voltmeter Selector Switch, Digital Ammeter - 96x96sq.mm., Ammeter Selector Switch CTs 6005A Cl-1, 15VA (Cast Resin),Phase Indicating lamp & On/Off Indicating Lamps
Outgoings
200A TPN MCCB 36kA with Microprocessor based release, aux. contact, 63A TPN MCCB 36kA with Microprocessor based release, aux. contact Nos. star delta starter (20HP) Feeder comprising of :-
63A TPN MCCB 36kA with Microprocessor based release , Contactor 25 A TP, Overload relay 14-23 A, Stardelta starter, Indicating Light, Push Button, Auto Manual Selector Switch, Control MCB , 10KA
35 | Providing and fixing resilient rubber lined neoprene single arch vibration eliminators with unit control suitable for fire pump upto 450 C. Temperature working pressure 20 Kg. per square centimeter .
a | 100 mm dia | Each | 2 |  |  | 0
b | 150 mm dia | Each | 6 |  |  | 0
36 | Providing and fixing heavy duty PVC insulated, PVC armoured aluminium conductor cables 1100V grade including necessary support clamps and connection lugs complete in all respects.
a | Power cable 3core 16 sqmm. | Meter | 64 |  |  | 0
b | Power cable 3.5 core 70 sqmm. | Meter | 46 |  |  | 0
HAND APPLIANCES
37 | Supply & Fixing ISI marked (IS:13849) Portable Fire Exitnguisher, ABC type capacity 5 kg, finished externally with red enamel paint, complete in all respects including initial fill and wall suspension. Capacity 5 kg | Each | 39 |  |  | 0
38 | Supply & Fixing ISI marked (IS:2878) Portable fire Extinguisher, Carbon‐dioxide type flat base including valve, discharge hose of not less than 10 mm dia. min. 600 mm long & complete in all respects including initial fill with C02 gas confirming to IS:307‐1966 filled to a filling ratio of not more than 0.667and wall suspension bracket. Capacity 4.5 Kg. | Each | 11 |  |  | 0
39 | Supply & Fixing ISI marked (IS:10204) Poratable Fire Exitnguisher,Trolley mounted Mech. Foam type capacity 09 ltrs with gun‐metal cap and nozzle and complete respects in all respects including initial fill and wall suspension.Capacity 9.0 ltrs | Each | 1 |  |  | 0
40 | Supply & Fixing of ISI marked (IS:2878) Fire Extinguisher, Trolley mounted, CO2 (gas pressure) type capacity 22.5 Kg. with gun‐metal cap. And nozzle and complete in all respects including initial fill and wall suspension bracket.Capacity 22.5 Kg. | Each | 1 |  |  | 0
FIRE ALARM SYSTEM
41 | Conventional fire alarm system: Erection ,testing and commissioning of 12 zone main fire alarm panel complete with battery charger with two nos 12 amp hr. 12V maintenance free batteries. | Each | 1 |  |  | 0
42 | Multi Sensor (Combination of Photoelectric & ROR Heat Detector) Supply & installation of Multi Sensor (Combination of Photoelectric & ROR Heat Detector) With Reponse indicator for a wide range of fire detection with enhanced immunity to nuisance particulates. | Each | 410 |  |  | 0
43 | Manual Call Point: Supply, installation, testing and commissioning of manual push button to initiate audio alarm with a breakable glass cover/ resettable, intelligent addressable type along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards. | Each | 36 |  |  | 0
44 | Hooter (Internal) : Supply, installation, testing and commissioning of Fire Alarm Hooter, intelligent, addressable, (sound output of minimum 90 dB upto a distance of 30 meters) with strobe light of 110 cd intensity with power supply arrangement along with accessories, hardwares etc as required for completeness and as per attached specification, direction of Engineer, CGPWD standards Electrical Inspectorate standards and suitable for wall/ceiling mounting and as per specifications. Colour of hooter to be approved by architect before placing the order. | Each | 36 |  |  | 0
45 | Installtion testing and commissioning of 2Cx1.5 sq. mm copper armoured shielded cable. | Mtr | 1700 |  |  | 0
| SUB TOTAL OF PART D : FIRE FIGHTING AND DETECTION WORKS |  |  |  |  | 0